FW Update for JBO

Open up ago Ethernet Update Software


[image: image1.png]A WAGO Ethernet Update !EE

WAGO Ethernet Update w
Version 1.3

42 H % 5 158

et Open S| Fimwse  Setings He\v
Please seloct a fimware i
] [ oaddiess | Networkname | Tiem o [SWerson | Progess | state T

There are no devices to shaw in this vien.

Carcel.

et [ er-correctors: 1 [ porangio | I





Select Firmware button and select the *.hex file sent.


[image: image2.png]- Address Range
& 1p-Addresses): From

NN
Tofez [z o [ash
T~ Enable network name resolution

" Network-hame(s):
EEmT—

~Device List

| Ip-Address | Network name | Item Ho. | MACID

oy | ol




Then Select Add and search for the controller within the IP range and once found select apply.


[image: image3.png]WAGO Ethernet Update

WAGO Ethernet Update

=lolx|

Jo woom m.mm
L] ‘ B = v €L

while updating the selected devices wi

'750-849_010129_00_old_style. hex’

progress

| 1P-Address. | Network name.

| Ttem Mo

| Swi-version | Progress | state

192.192.8.156

Cancel

‘

750849

01.01.23(00) Shutdonn programs

Update s in progress

[ Comeetos

1

[ Pending: 1| — |





Then press the update button…

The I/O light will flash Yellow. Important not to disconnect the Ethernet lead, let laptop go into standby or lose power to the controller.

Once complete you will see the below screen-


[image: image4.png]WAGO Ethernet Update

Version 1.3
4 2 H ‘ v %R ‘
ERN

ith '750-849_010129_00,

The selected devices was uptated

[ | 1p-address. | Networkname | Item ho. | Swi-version | Progress | State

[ 152192.8.15 750643 01.01.25(00) TR Upsated n 1215





After a FW update the below will have happened

IP address should still be the same.
Date and Time still the same

CoDeSys Programme removed
Controller KNX Address removed
Controller Application removed
Router KNX address removed
Router KNX Application removed
Steps to take and order:-
1. Login with CoDeSys and create Bootproject

2. Address the IP controller in ETS
3. Download IP Controller application from ETS

4. Address the IP router in ETS

5. Download IP Controller application from ETS

6. Log In with CoDeSys and ensure you see “KNX OK” out of FbKNX_Master_849”

7. Reset all PIRs from ETS.

If you don’t see KNX OK make sure that the SYM_XML is the correct one selected.
_1390805530.bin

_1390805653.bin

_1390805842.bin

_1390805445.bin

