## Index
Modular Systems + | [6 empty] | The ARK Electrical Design Co.
Fife New Hospital Joint Venture
Cable Calculation Index
Project Name: |  | Fife-JV |  |  |  | Date: | 08.10.10
Project Nº: |  | MW502 |  |  |  | By: | N Holmes
Area/Zone/Level: |  | Level 01 - DB Zone E5¦1¦BP
Drawing Nº: |  | CD-MS-XX-L(62)-0-XX-001 Rev B
Service: |  | Power
Nominal Voltage: |  | 230
Max Volt Drop: |  | 4%
Distribution Board Data |  |  | L1 | L2 | L3
DB Ref: |  | E5¦1¦BP
Voltage Drop: |  |  | 0.08% | 0.08% | 0.08%
Final Voltage: |  |  | 5.98 | 5.98 | 5.98
Ipsc (Max): |  | 5800
Ipsc (Min): |  | 1500
Zs: |  | 0.2
| MDB Nº |  | Circuit Ref |  |  | Legs
| 05 |  | 9L1 |  |  | a
| "" |  | 10L2 |  |  | a
| "" |  | 9L3 |  |  | a
| "" |  | 10L3 |  |  | a
Notes:
1. | Where conntection points/outlets are located within the Ceiling Void (CV), no Service Drop (SD) is shown.

## Load Schedule
Modular Systems + |  |  |  |  | The ARK Electrical Design Co.
Fife New Hospital Joint Venture
Load Schedule |  |  | Date: | 08.10.10
Project Name: |  | Fife-JV | By: | N Holmes
Project Nº: |  | MW502
Area/Zone/Level: |  | Level 01 - DB Zone E5¦1¦BP
Drawing Nº: |  | CD-MS-XX-L(62)-0-XX-001 Rev B
Service: |  | Power
H+K Ref |  | Item |  | Load
01 |  | Fridge | 300 | per point
02 |  | Freezer | 300 | per point
03 |  | Water Cooler | 300 | per point
04 |  | Water Boiler | 3000 | per point
05 |  | Fume Cabinet
06 |  | Storage Cabinet
07 |  | X-Ray Viewer | 50 | per point
08 |  | Fan Coil Unit | 600 | per point
09 |  | LCD Projector
10 |  | -
11 |  | -
12 |  | Docking Station
13 |  | Macerator | 100 | per point
14 |  | Pneumatic Tube
15 |  | Patient Hoist
16 |  | Examination Lamp
17 |  | Ice Maker | 500 | per point
18 |  | Heated Cabinet
19 |  | Patient Entertainment | 150 | per point
20 |  | Regen Trolley
21 |  | Vending Machine
22 |  | Incubator
23 |  | Microscope
24 |  | Entry Sign
25 |  | Gas Solenoid
H+K Ref |  | Item |  | Load
26 |  | -
27 |  | Insect Killer | 50 | per point
28 |  | Water Softener
29 |  | Post Mortem Table
30 |  | Plasma TV
31 |  | Peninsular Bath | 300 | per point
32 |  | Air Curtain
33 |  | Induction Loop | 50 | per point
34 |  | Dishwasher | 3000 | per point
34 |  | Washing Machine | 1200 | per point
35 |  | Gamma Camera
36 |  | Media Wall
37 |  | Gas Plasma Steriliser
38 |  | Platelet Agitator
39 |  | Alarm/Control Panel
40 |  | Blood Gas Analyser
41 |  | Heat Sealing Machine
42 |  | Iron
43 |  | Sewing Machine
44 |  | Misc Lab Equip
45 |  | CCTV Camera | 150 | per point
46 |  | Gas Cooker
47 |  | VAV Terminal
48 |  | Patient Inf Sys Panel
49 |  | Extract Hood
H+K Ref |  | Item |  | Load
50 |  | PUVA Booth
51 |  | Powered Chair
52 |  | Snellen Chart (Right)
53 |  | Sump Pump
54 |  | Scale Inhibitor
55 |  | PD Warming Cupboard
56 |  | Entertainment Card Disp
57 |  | Bar Code Reader
58 |  | Powered Chair
59 |  | Snellen Chart (Left)
60 |  | Heamatology Machine
61 |  | Electronic Notice Board
62 |  | Blanket Warmer
63 |  | Staff Call PSU
64 |  | Microwave Oven | 800 | per point
65 |  | BMS Outstation
66 |  | Pneumatic Tube Station
67 |  | Fire Alarm Interface | 100 | per point
68 |  | Waste Disposal
69 |  | Centrifuge
70 |  | Griddle Plate
71 |  | Deep Fat Fryer
72 |  | Heated Towel Rail
73 |  | Dis Refuge Intercom
74 |  | Tubular Heater
H+K Ref |  | Item |  | Load
75 |  | System Control (PTS)
76 |  | System VO (PTS)
77 |  | Security Access Control | 100 | per point
78 |  | Security Intercom
79 |  | CCTV Monitor
80 |  | Local CCTV
81 |  | Eng Fire Alarm Panel
82 |  | Fire Alarm Panel
83 |  | Security Control Panel
84 |  | Security IO & PA
|  | Cleaners Socket | 3000 | (last outlet only)
|  | External Socket | 3680 | per point
- |  | Food Trolley | 1800 | per point
- |  | Toaster | 1100 | per point
| Tumble Dryer |  | 2200 | per point
| Ventilation Fan |  | 200 | per point
| Roller Shutter |  | 500 | per point
| Maglock |  | 100 | per point
| Door Detente |  | 100 | per point
| Intercom |  | 100 | per point
| Measurement Machine |  | 100 | per point
| Drugs Cupboard |  | 100 | per point
| Sanitiser Pump |  | 300 | per point
| TV Amplifier |  | 100 | per point

## 9L1
Modular Systems + | [7 empty] | © The ARK Electrical Design Co. 2009 | Modular Systems + | [9 empty] | © The ARK Electrical Design Co. 2009 | [15 empty] | Tabulated Zs Figures for 5 Second Disconnection Time | [10 empty] | Tabulated Zs Figures for 0.4 Second Disconnection Time
[29 empty] | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
CIRCUIT CALCULATION SHEET: | [8 empty] | CIRCUIT CALCULATION SHEET: | [13 empty] | Short-Circuit Withstand | [7 empty] | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D |  |  | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
Project Name: |  | Fife-JV |  |  |  | Prepared By: | N Holmes |  | Project Name: |  | Fife-JV | [5 empty] | Prepared By: | N Holmes |  |  |  |  | Is Ipsc trip time > 0.1s | [5 empty] | 6A | B | 8 | 7.7 |  |  | 8.8 |  | 7.6 |  |  | 6A | B | 8 | 7.7 |  |  | 8 |  | 7.6
Project Nº: |  | MW502 |  |  |  | Date Prepared: | 08.10.10 |  | Project Nº: |  | MW502 | [5 empty] | Date Prepared: | 08.10.10 |  |  |  |  | If YES, then I²S² from ABB required |  | HOMERUN | EXTENDER | SERVICE DROP |  | " | C | 4 | 3.8 |  |  | 8.8 |  | 4.89 |  |  | " | C | 4 | 3.8 |  |  | 4 |  | 3.88
Area/Zone/Level: |  | Level 01 - DB Zone E5¦1¦BP |  |  |  | Revision: | B |  | Area/Zone/Level: |  | Level 01 - DB Zone E5¦1¦BP | [5 empty] | Revision: | B |  |  |  |  | K²S²>A²s | It (Tab): | 32 | 32 | 25 |  | " | D | 2 | 2.7 |  |  | 8.8 |  | 4.89 |  |  | " | D | 2 | 2.7 |  |  | 1 |  | 2.74
Drawing Nº: |  | CD-MS-XX-L(62)-0-XX-001 Rev B |  |  |  | Checked By: | N Holmes |  | Drawing Nº: |  | CD-MS-XX-L(62)-0-XX-001 Rev B | [5 empty] | Checked By: | N Holmes |  |  |  |  | Establish the typical range of A²s from ABB for the range of Ipsc | [5 empty] | 10A | B | 4.8 | 4.6 |  |  | 5.33 |  | 4.6 |  |  | 10A | B | 4.8 | 4.6 |  |  | 4.8 |  | 4.6
Service: |  | Power |  |  |  |  | UCVD Aug 2009 V4.2 |  | Service: |  | Power | [6 empty] | UCVD Aug 2009 V4.2 | [5 empty] | Voltage Drop (Tab): | 11 | 12 | 19 |  | " | C | 2.4 | 2.2 |  |  | 5.33 |  | 2.95 |  |  | " | C | 2.4 | 2.2 |  |  | 2.4 |  | 2.3
[29 empty] | " | D | 1.2 | 1.6 |  |  | 5.33 |  | 2.95 |  |  | " | D | 1.2 | 1.6 |  |  | 1.2 |  | 1.64
DB Ref: |  | E5¦1¦BP | [6 empty] | DB Ref: |  | E5¦1¦BP | [12 empty] | R@20²C (Tab): | 4.61 | 5.6 | 7.98 |  | 16A | B | 3 | 2.9 |  |  | 3.33 |  | 2.88 |  |  | 16A | B | 3 | 2.9 |  |  | 3 |  | 2.88
MDB Nº: |  | E5¦1¦BP¦05 | [6 empty] | MDB Nº: |  | E5¦1¦BP¦05 | [17 empty] | " | C | 1.5 | 1.4 |  |  | 3.33 |  | 1.84 |  |  | " | C | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
Circuit Ref: |  | E5¦1¦BP¦9L1 | [6 empty] | Circuit Ref: |  | E5¦1¦BP¦9L1 | [12 empty] | Zinst_PHASE: | 5.7533 | 6.9888 | 9.959 |  | " | D | 0.75 | 1 |  |  | 3.33 |  | 1.84 |  |  | " | D | 0.75 | 1 |  |  | 0.75 |  | 1.03
[24 empty] | Zinst_CPC: | 5.7533 | 6.9888 | 9.959 |  | 20A | B | 2.4 | 2.3 |  |  | 2.66 |  | 2.3 |  |  | 20A | B | 2.4 | 2.3 |  |  | 2.4 |  | 2.3
DISTRIBUTION BOARD: |  |  |  |  | HOMERUN CABLE: |  |  |  | CIRCUIT INPUT DATA: | [19 empty] | " | C | 1.2 | 1.2 |  |  | 2.66 |  | 1.47 |  |  | " | C | 1.2 | 1.2 |  |  | 1.2 |  | 1.15
Voltage Drop: |  |  | 0.08 | % | Nº of Circuits per MDB: |  | 9 | [16 empty] | CPD_R_Factor: | 1.248 | 1.248 | 1.248 |  | " | D | 0.6 | 0.8 |  |  | 2.66 |  | 1.47 |  |  | " | D | 0.6 | 0.8 |  |  | 0.6 |  | 0.82
Actual Voltage: |  |  | 224.02 | V | CSA: |  | 4 | mm² | CABLE | CABLE | LENGTH | LOAD (A) |  |  | VOLTAGE DROP (V) |  | Zs | Ipsc | [10 empty] | 25A | B | 1.8 | 1.8 |  |  | 2.14 |  | 1.84 |  |  | 25A | B | 1.8 | 1.8 |  |  | 1.92 |  | 1.84
Fault Current @ DB (Ipsc): |  |  | 5800 | A | Insulation: |  | LSFZH |  | TYPE | LEG | Metres | Per Leg | Total | Per Leg | Total | % | (W) | (A) |  | Zs | Ipsc | %VoltDrop |  | Ambient T (IEE GN5 Table B1): | 1.04 | 1.04 | 1.04 |  | " | C | 1 | 0.9 |  |  | 2.14 |  | 1.18 |  |  | " | C | 1 | 0.9 |  |  | 0.96 |  | 0.92
External P/E Loop (Ze): |  |  | 0.2 | Ω | Operating Temperature (tp): |  | 70 | °C | Home Run | - | 0 | - | 15.66 | 0 | 0 | 0 | 0.2 | 5800 |  | 0.2 | 5800 | 0 |  | Temp Factor F (IEE GN5 Table B2): | 1.2 | 1.2 | 1.2 |  | " | D | 0.46 | 0.7 |  |  | 2.14 |  | 1.18 |  |  | " | D | 0.46 | 0.7 |  |  | 0.48 |  | 0.66
[5 empty] | Rating (It): |  | 32 | A | U | 1 | 35 | 5.2174 | 15.66 | 10.4139 | 10.4139 | 4.53 | 0.69 | 434.8885 |  | 0.49 | -5365.1115 | 4.53 |  | Total Factor: | 1.248 | 1.248 | 1.248 |  | 32A | B | 1.5 | 1.4 |  |  | 1.66 |  | 1.44 |  |  | 32A | B | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
[5 empty] | Volt Drop (R): |  | 11 | mV/A/m | U | 2 | 22 | 5.2174 | 10.44 | 4.3639 | 14.7778 | 6.43 | 1 | 274.9952 |  | 0.31 | -159.8934 | 1.9 | [6 empty] | " | C | 0.75 | 0.7 |  |  | 1.66 |  | 0.92 |  |  | " | C | 0.75 | 0.7 |  |  | 0.75 |  | 0.72
CIRCUIT DESIGN: |  |  |  |  | R @ 20°c: |  | 4.61 | Ω/km | U | 3 | 9 | 5.2174 | 5.22 | 0.8926 | 15.6704 | 6.82 | 1.13 | 239.0413 |  | 0.13 | -35.9538 | 0.39 | [6 empty] | " | D | 0.38 | 0.5 |  |  | 1.66 |  | 0.92 |  |  | " | D | 0.38 | 0.5 |  |  | 0.37 |  | 0.51
Nominal Voltage (V): |  |  | 230 | V | Phase-Earth Loop Impedance: |  | 11.51 | Ω/km |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Insulation Working Temp (tp): | 70 | 70 | 70 | °c
Homerun Cable Length: |  |  |  | m | Ipsc: |  | 5800 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Insulation Final Limit Temp: | 160 | 160 | 160 | °c
Max VD: |  |  | 3.92 | % | I²t or A²s: |  | 10000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Disconnection Time: |  |  | 0.4 | s | K²S²: |  | 327184 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Grouping Factor: | 0.5 | 0 | 1
[5 empty] | K²S²>I²t or A²s: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0.71 | 0.71
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Cg: | 0.5 | 0.71 | 1.71
CIRCUIT PROTECTIVE DEVICE (CPD): | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Rating (In): |  |  | 20 | A | ARMOURED EXTENDER CABLE: | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | It ≥ | 40 | 28.169 | 11.6959 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Type (MCB Only): |  |  | C |  | Nº of Circuits/Cables: |  | 10 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manufacturer: |  |  | Hager |  | CSA: |  | 4 | mm² |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | CPD: | Hager | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tabulated Zs: |  |  | 1.2 | Ω | Insulation: |  | LSFZH | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 5 Sec | 2.66 | [5 empty] | 1.2 | 1.2 | 0 | 0 | 2.66 | 0 | 1.47 | 0 | 0 |  |  | 1.2 | 1.2 | 0 | 0 | 1.2 | 0 | 1.15 | 0 | 0
[5 empty] | Operating Temperature (tp): |  | 70 | °C |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0.4 Sec | 1.2 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Rating (It): |  | 32 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Zs: | 1.2 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Volt Drop (R): |  | 12 | mV/A/m |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | CPD | 1.2 | 1.2 | 0 | 0 | 2.66 | 0 | 1.47 | 0 | 0 |  | CPD | 1.2 | 1.2 | 0 | 0 | 1.2 | 0 | 1.15 | 0 | 0
[5 empty] | R @ 20°c: |  | 5.6 | Ω/km |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail MDB Cg: | û
[5 empty] | Phase-Earth Loop Impedance: |  | 13.98 | Ω/km |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Cg: |  | ü |  |  |  | Hager | [10 empty] | Hager
[5 empty] | Ipsc Max: |  | 434.8885 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Cg: |  |  | ü
| 0 |  |  |  | Ipsc Min: |  | 239.0413 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail VD: | û | ü | ü
[5 empty] | I²t or A²s Max: |  | 980 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Zs: | ü | û | û |  |  |  | 20A Type C |  | 10A Type C
[5 empty] | I²t or A²s Min: |  | 300 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SWITCH DROP/UN-ARMOURED CABLE: | Pass/Fail Home-Run Ipsc: | ü | [5 empty] | Ipsc | A²s | Ipsc | A²s
[5 empty] | K²S²: |  | 327184 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SERVICE DROP CABLE: | Pass/Fail Extender Max Ipsc: | ü
[5 empty] | K²S²>I²t or A²s Max: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Min Ipsc: | ü |  |  |  |  | 1 | 100 | 70 | 100 | 70
[5 empty] | K²S²>I²t or A²s Min: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Ipsc: | ü |  |  |  |  | 2 | 200 | 300 | 200 | 300
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | 3 | 300 | 500 | 300 | 500
[20 empty] | 1.13 | 239.0413 | 6.82 |  | Supply Voltage Drop: | 0.08% |  |  |  |  | 4 | 400 | 980 | 400 | 980
[5 empty] | SERVICE DROP CABLE: |  |  |  | KEY: | [5 empty] | CIRCUIT CHECK: |  |  | OK | [5 empty] | Supply Voltage Drop: | 5.98 |  |  |  |  | 5 | 500 | 1200 | 500 | 1200
[5 empty] | Nº of Circuits/Cables: |  | 1 |  | A = Armoured Extender Cable | [5 empty] | Homerun Overload Protection: |  |  | û | [11 empty] | 6 | 600 | 1500 | 600 | 1500
[5 empty] | CSA: |  | 2.5 | mm² | D = Service or Switch Drop | [5 empty] | Extender Overload Protection: |  |  | ü | [6 empty] | 3.92 |  |  |  |  | 7 | 700 | 2000 | 700 | 2000
[5 empty] | Insulation: |  | LSFZH |  | F = Flying Lead | [5 empty] | SD/RL Overload Protection: |  |  | ü | [11 empty] | 8 | 800 | 2100 | 800 | 2100
[5 empty] | Operating Temperature (tp): |  | 70 | °C | S = Splitter/Tee | [5 empty] | Voltage Drop less than 3.92%: |  |  | û | [11 empty] | 9 | 900 | 2500 | 900 | 2500
[5 empty] | Rating (It): |  | 25 | A | U = Armoured Extender Cable | [5 empty] | Calculated Zs less than Tab Zs: |  |  | ü | [11 empty] | 10 | 1000 | 2800 | 1000 | 2800
[5 empty] | Volt Drop (R): |  | 19 | mV/A/m | [21 empty] | 11 | 2000 | 6000 | 2000 | 6000
[5 empty] | R @ 20°c: |  | 7.98 | Ω/km | [21 empty] | 12 | 3000 | 8400 | 3000 | 8400
| RESULTS SUMMARY |  |  |  | Phase-Earth Loop Impedance: |  | 19.92 | Ω/km | [21 empty] | 13 | 4000 | 10000 | 4000 | 10000
| Load: |  | 15.66 |  | Ipsc: |  | 239.0413 | A | NOTES:
| Length: |  | 66 |  | I²t or A²s: |  | 300 |  | 1. Based upon Ambient Temperature of 30°C.
| Zs: |  | 1.13 |  | K²S²: |  | 127806.25 |  | 2. Zs vaule @ source based upon Transfomrer Supply. | [20 empty] | Home-Run: | 5800
| Ipsc: |  | 239.0413 |  | K²S²>I²t or A²s: |  | ü |  | 3. Ipsc vaule @ source based upon Transformer Supply (max figure). | [20 empty] | Extender Max: | 434.8885 |  | Thermal Withstand Model
| Voltage Drop: |  | 15.6704 | [5 empty] | 4. Thermal-Withstand current levels taken at MDB, end of 1st Extender & end of circuit leg. | [20 empty] | Extender Min: | 239.0413
| Final Voltage: |  | 208.3496 | [26 empty] | SD: | 239.0413
[31 empty] | Home-Run |  | Extender Max |  | Extender Min
[30 empty] | 13 | 10000 |  | 0 |  | 0
[30 empty] | 12 | 0 |  | 0 |  | 0
[30 empty] | 11 | 0 |  | 0 |  | 0
[30 empty] | 10 | 0 |  | 0 |  | 0
[30 empty] | 9 | 0 |  | 0 |  | 0
[30 empty] | 8 | 0 |  | 0 |  | 0
[30 empty] | 7 | 0 |  | 0 |  | 0
[30 empty] | 6 | 0 |  | 0 |  | 0
[30 empty] | 5 | 0 |  | 0 |  | 0
[30 empty] | 4 | 0 |  | 980 |  | 0
[30 empty] | 3 | 0 |  | 0 |  | 0
[30 empty] | 2 | 0 |  | 0 |  | 300
[30 empty] | 1 | 0 |  | 0 |  | 0
[30 empty] | Value: | 10000 |  | 980 |  | 300
Note on J15: Enter nº of circuits at MDB (max = 9). This value MUST include all spare capacity.
Note on J16: Enter: 2.50 4.00 6.00
Note on J17: Enter: XL-LSFZH LSFZH
Note on D30: Enter: B C D
Note on J30: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on D31: Enter: BS7671 ABB Hager Schneider
Note on J31: Enter: 1.50 2.50 4.00
Note on J32: Enter: XL-LSFZH LSFZH
Note on J48: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on J49: Enter: 1.50 2.50 4.00
Note on J50: Enter: XL-LSFZH LSFZH

## 10L2
Modular Systems + | [7 empty] | © The ARK Electrical Design Co. 2009 | Modular Systems + | [9 empty] | © The ARK Electrical Design Co. 2009 | [15 empty] | Tabulated Zs Figures for 5 Second Disconnection Time | [10 empty] | Tabulated Zs Figures for 0.4 Second Disconnection Time
[29 empty] | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
CIRCUIT CALCULATION SHEET: | [8 empty] | CIRCUIT CALCULATION SHEET: | [13 empty] | Short-Circuit Withstand | [7 empty] | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D |  |  | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
Project Name: |  | Fife-JV |  |  |  | Prepared By: | N Holmes |  | Project Name: |  | Fife-JV | [5 empty] | Prepared By: | N Holmes |  |  |  |  | Is Ipsc trip time > 0.1s | [5 empty] | 6A | B | 8 | 7.7 |  |  | 8.8 |  | 7.6 |  |  | 6A | B | 8 | 7.7 |  |  | 8 |  | 7.6
Project Nº: |  | MW502 |  |  |  | Date Prepared: | 08.10.10 |  | Project Nº: |  | MW502 | [5 empty] | Date Prepared: | 08.10.10 |  |  |  |  | If YES, then I²S² from ABB required |  | HOMERUN | EXTENDER | SERVICE DROP |  | " | C | 4 | 3.8 |  |  | 8.8 |  | 4.89 |  |  | " | C | 4 | 3.8 |  |  | 4 |  | 3.88
Area/Zone/Level: |  | Level 01 - DB Zone E5¦1¦BP |  |  |  | Revision: | B |  | Area/Zone/Level: |  | Level 01 - DB Zone E5¦1¦BP | [5 empty] | Revision: | B |  |  |  |  | K²S²>A²s | It (Tab): | 32 | 32 | 25 |  | " | D | 2 | 2.7 |  |  | 8.8 |  | 4.89 |  |  | " | D | 2 | 2.7 |  |  | 1 |  | 2.74
Drawing Nº: |  | CD-MS-XX-L(62)-0-XX-001 Rev B |  |  |  | Checked By: | N Holmes |  | Drawing Nº: |  | CD-MS-XX-L(62)-0-XX-001 Rev B | [5 empty] | Checked By: | N Holmes |  |  |  |  | Establish the typical range of A²s from ABB for the range of Ipsc | [5 empty] | 10A | B | 4.8 | 4.6 |  |  | 5.33 |  | 4.6 |  |  | 10A | B | 4.8 | 4.6 |  |  | 4.8 |  | 4.6
Service: |  | Power |  |  |  |  | UCVD Aug 2009 V4.2 |  | Service: |  | Power | [6 empty] | UCVD Aug 2009 V4.2 | [5 empty] | Voltage Drop (Tab): | 11 | 12 | 19 |  | " | C | 2.4 | 2.2 |  |  | 5.33 |  | 2.95 |  |  | " | C | 2.4 | 2.2 |  |  | 2.4 |  | 2.3
[29 empty] | " | D | 1.2 | 1.6 |  |  | 5.33 |  | 2.95 |  |  | " | D | 1.2 | 1.6 |  |  | 1.2 |  | 1.64
DB Ref: |  | E5¦1¦BP | [6 empty] | DB Ref: |  | E5¦1¦BP | [12 empty] | R@20²C (Tab): | 4.61 | 5.6 | 7.98 |  | 16A | B | 3 | 2.9 |  |  | 3.33 |  | 2.88 |  |  | 16A | B | 3 | 2.9 |  |  | 3 |  | 2.88
MDB Nº: |  | E5¦1¦BP¦05 | [6 empty] | MDB Nº: |  | E5¦1¦BP¦05 | [17 empty] | " | C | 1.5 | 1.4 |  |  | 3.33 |  | 1.84 |  |  | " | C | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
Circuit Ref: |  | E5¦1¦BP¦10L2 | [6 empty] | Circuit Ref: |  | E5¦1¦BP¦10L2 | [12 empty] | Zinst_PHASE: | 5.7533 | 6.9888 | 9.959 |  | " | D | 0.75 | 1 |  |  | 3.33 |  | 1.84 |  |  | " | D | 0.75 | 1 |  |  | 0.75 |  | 1.03
[24 empty] | Zinst_CPC: | 5.7533 | 6.9888 | 9.959 |  | 20A | B | 2.4 | 2.3 |  |  | 2.66 |  | 2.3 |  |  | 20A | B | 2.4 | 2.3 |  |  | 2.4 |  | 2.3
DISTRIBUTION BOARD: |  |  |  |  | HOMERUN CABLE: |  |  |  | CIRCUIT INPUT DATA: | [19 empty] | " | C | 1.2 | 1.2 |  |  | 2.66 |  | 1.47 |  |  | " | C | 1.2 | 1.2 |  |  | 1.2 |  | 1.15
Voltage Drop: |  |  | 0.08 | % | Nº of Circuits per MDB: |  | 9 | [16 empty] | CPD_R_Factor: | 1.248 | 1.248 | 1.248 |  | " | D | 0.6 | 0.8 |  |  | 2.66 |  | 1.47 |  |  | " | D | 0.6 | 0.8 |  |  | 0.6 |  | 0.82
Actual Voltage: |  |  | 224.02 | V | CSA: |  | 4 | mm² | CABLE | CABLE | LENGTH | LOAD (A) |  |  | VOLTAGE DROP (V) |  | Zs | Ipsc | [10 empty] | 25A | B | 1.8 | 1.8 |  |  | 2.14 |  | 1.84 |  |  | 25A | B | 1.8 | 1.8 |  |  | 1.92 |  | 1.84
Fault Current @ DB (Ipsc): |  |  | 5800 | A | Insulation: |  | LSFZH |  | TYPE | LEG | Metres | Per Leg | Total | Per Leg | Total | % | (W) | (A) |  | Zs | Ipsc | %VoltDrop |  | Ambient T (IEE GN5 Table B1): | 1.04 | 1.04 | 1.04 |  | " | C | 1 | 0.9 |  |  | 2.14 |  | 1.18 |  |  | " | C | 1 | 0.9 |  |  | 0.96 |  | 0.92
External P/E Loop (Ze): |  |  | 0.2 | Ω | Operating Temperature (tp): |  | 70 | °C | Home Run | - | 58 | - | 10.43 | 6.6543 | 6.6543 | 2.9 | 0.87 | 326 |  | 0.87 | 326 | 2.9 |  | Temp Factor F (IEE GN5 Table B2): | 1.2 | 1.2 | 1.2 |  | " | D | 0.46 | 0.7 |  |  | 2.14 |  | 1.18 |  |  | " | D | 0.46 | 0.7 |  |  | 0.48 |  | 0.66
[5 empty] | Rating (It): |  | 32 | A | A | 1 | 5 |  | 10.43 | 0.6258 | 7.2801 | 3.17 | 0.94 | 296.6175 |  | 0.07 | -29.3825 | 0.27 |  | Total Factor: | 1.248 | 1.248 | 1.248 |  | 32A | B | 1.5 | 1.4 |  |  | 1.66 |  | 1.44 |  |  | 32A | B | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
[5 empty] | Volt Drop (R): |  | 11 | mV/A/m | A | 2 | 10 |  | 10.43 | 1.2516 | 8.5317 | 3.71 | 1.08 | 251.3152 |  | 0.14 | -45.3023 | 0.54 | [6 empty] | " | C | 0.75 | 0.7 |  |  | 1.66 |  | 0.92 |  |  | " | C | 0.75 | 0.7 |  |  | 0.75 |  | 0.72
CIRCUIT DESIGN: |  |  |  |  | R @ 20°c: |  | 4.61 | Ω/km | A | 3 | 10 |  | 10.43 | 1.2516 | 9.7833 | 4.26 | 1.22 | 218.0174 |  | 0.14 | -33.2977 | 0.55 | [6 empty] | " | D | 0.38 | 0.5 |  |  | 1.66 |  | 0.92 |  |  | " | D | 0.38 | 0.5 |  |  | 0.37 |  | 0.51
Nominal Voltage (V): |  |  | 230 | V | Phase-Earth Loop Impedance: |  | 11.51 | Ω/km | D | 4 | 10 | 10.4348 | 10.43 | 1.9817 | 11.765 | 5.12 | 1.36 | 192.5109 |  | 0.14 | -25.5065 | 0.86 |  | Insulation Working Temp (tp): | 70 | 70 | 70 | °c
Homerun Cable Length: |  |  | 58 | m | Ipsc: |  | 326 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Insulation Final Limit Temp: | 160 | 160 | 160 | °c
Max VD: |  |  | 3.92 | % | I²t or A²s: |  | 500 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Disconnection Time: |  |  | 0.4 | s | K²S²: |  | 327184 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Grouping Factor: | 0.5 | 0 | 1
[5 empty] | K²S²>I²t or A²s: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0.71 | 0.71
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Cg: | 0.5 | 0.71 | 1.71
CIRCUIT PROTECTIVE DEVICE (CPD): | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Rating (In): |  |  | 20 | A | ARMOURED EXTENDER CABLE: | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | It ≥ | 40 | 28.169 | 11.6959 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Type (MCB Only): |  |  | B |  | Nº of Circuits/Cables: |  | 10 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manufacturer: |  |  | ABB |  | CSA: |  | 4 | mm² |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | CPD: | ABB | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tabulated Zs: |  |  | 2.3 | Ω | Insulation: |  | LSFZH | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 5 Sec | 2.3 | [5 empty] | 2.4 | 2.3 | 0 | 0 | 2.66 | 0 | 2.3 | 0 | 0 |  |  | 2.4 | 2.3 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
[5 empty] | Operating Temperature (tp): |  | 70 | °C |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0.4 Sec | 2.3 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Rating (It): |  | 32 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Zs: | 2.3 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Volt Drop (R): |  | 12 | mV/A/m |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | CPD | 2.4 | 2.3 | 0 | 0 | 2.66 | 0 | 2.3 | 0 | 0 |  | CPD | 2.4 | 2.3 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
[5 empty] | R @ 20°c: |  | 5.6 | Ω/km |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail MDB Cg: | û
[5 empty] | Phase-Earth Loop Impedance: |  | 13.98 | Ω/km |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Cg: |  | ü |  |  |  | ABB | [10 empty] | ABB
[5 empty] | Ipsc Max: |  | 296.6175 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Cg: |  |  | ü
| 0 |  |  |  | Ipsc Min: |  | 192.5109 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail VD: | û | ü | ü
[5 empty] | I²t or A²s Max: |  | 300 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Zs: | ü | û | û |  |  |  | 20A Type C |  | 10A Type C
[5 empty] | I²t or A²s Min: |  | 70 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SWITCH DROP/UN-ARMOURED CABLE: | Pass/Fail Home-Run Ipsc: | ü | [5 empty] | Ipsc | A²s | Ipsc | A²s
[5 empty] | K²S²: |  | 327184 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SERVICE DROP CABLE: | Pass/Fail Extender Max Ipsc: | ü
[5 empty] | K²S²>I²t or A²s Max: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Min Ipsc: | ü |  |  |  |  | 1 | 100 | 70 | 100 | 70
[5 empty] | K²S²>I²t or A²s Min: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Ipsc: | ü |  |  |  |  | 2 | 200 | 300 | 200 | 300
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | 3 | 300 | 500 | 300 | 500
[20 empty] | 1.36 | 192.5109 | 5.12 |  | Supply Voltage Drop: | 0.08% |  |  |  |  | 4 | 400 | 980 | 400 | 980
[5 empty] | SERVICE DROP CABLE: |  |  |  | KEY: | [5 empty] | CIRCUIT CHECK: |  |  | OK | [5 empty] | Supply Voltage Drop: | 5.98 |  |  |  |  | 5 | 500 | 1200 | 500 | 1200
[5 empty] | Nº of Circuits/Cables: |  | 1 |  | A = Armoured Extender Cable | [5 empty] | Homerun Overload Protection: |  |  | û | [11 empty] | 6 | 600 | 1500 | 600 | 1500
[5 empty] | CSA: |  | 2.5 | mm² | D = Service or Switch Drop | [5 empty] | Extender Overload Protection: |  |  | ü | [11 empty] | 7 | 700 | 2000 | 700 | 2000
[5 empty] | Insulation: |  | LSFZH |  | F = Flying Lead | [5 empty] | SD/RL Overload Protection: |  |  | ü | [11 empty] | 8 | 800 | 2100 | 800 | 2100
[5 empty] | Operating Temperature (tp): |  | 70 | °C | S = Splitter/Tee | [5 empty] | Voltage Drop less than 3.92%: |  |  | û | [11 empty] | 9 | 900 | 2500 | 900 | 2500
[5 empty] | Rating (It): |  | 25 | A | U = Armoured Extender Cable | [5 empty] | Calculated Zs less than Tab Zs: |  |  | ü | [11 empty] | 10 | 1000 | 2800 | 1000 | 2800
[5 empty] | Volt Drop (R): |  | 19 | mV/A/m | [21 empty] | 11 | 2000 | 6000 | 2000 | 6000
[5 empty] | R @ 20°c: |  | 7.98 | Ω/km | [21 empty] | 12 | 3000 | 8400 | 3000 | 8400
| RESULTS SUMMARY |  |  |  | Phase-Earth Loop Impedance: |  | 19.92 | Ω/km | [21 empty] | 13 | 4000 | 10000 | 4000 | 10000
| Load: |  | 10.43 |  | Ipsc: |  | 192.5109 | A | NOTES:
| Length: |  | 93 |  | I²t or A²s: |  | 70 |  | 1. Based upon Ambient Temperature of 30°C.
| Zs: |  | 1.36 |  | K²S²: |  | 127806.25 |  | 2. Zs vaule @ source based upon Transfomrer Supply. | [20 empty] | Home-Run: | 326
| Ipsc: |  | 192.5109 |  | K²S²>I²t or A²s: |  | ü |  | 3. Ipsc vaule @ source based upon Transformer Supply (max figure). | [20 empty] | Extender Max: | 296.6175 |  | Thermal Withstand Model
| Voltage Drop: |  | 11.765 | [5 empty] | 4. Thermal-Withstand current levels taken at MDB, end of 1st Extender & end of circuit leg. | [20 empty] | Extender Min: | 192.5109
| Final Voltage: |  | 212.255 | [26 empty] | SD: | 192.5109
[31 empty] | Home-Run |  | Extender Max |  | Extender Min
[30 empty] | 13 | 0 |  | 0 |  | 0
[30 empty] | 12 | 0 |  | 0 |  | 0
[30 empty] | 11 | 0 |  | 0 |  | 0
[30 empty] | 10 | 0 |  | 0 |  | 0
[30 empty] | 9 | 0 |  | 0 |  | 0
[30 empty] | 8 | 0 |  | 0 |  | 0
[30 empty] | 7 | 0 |  | 0 |  | 0
[30 empty] | 6 | 0 |  | 0 |  | 0
[30 empty] | 5 | 0 |  | 0 |  | 0
[30 empty] | 4 | 0 |  | 0 |  | 0
[30 empty] | 3 | 500 |  | 0 |  | 0
[30 empty] | 2 | 0 |  | 300 |  | 0
[30 empty] | 1 | 0 |  | 0 |  | 70
[30 empty] | Value: | 500 |  | 300 |  | 70
Note on J15: Enter nº of circuits at MDB (max = 9). This value MUST include all spare capacity.
Note on J16: Enter: 2.50 4.00 6.00
Note on J17: Enter: XL-LSFZH LSFZH
Note on D30: Enter: B C D
Note on J30: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on D31: Enter: BS7671 ABB Hager Schneider
Note on J31: Enter: 1.50 2.50 4.00
Note on J32: Enter: XL-LSFZH LSFZH
Note on J48: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on J49: Enter: 1.50 2.50 4.00
Note on J50: Enter: XL-LSFZH LSFZH

## 9L3
Modular Systems + | [7 empty] | © The ARK Electrical Design Co. 2009 | Modular Systems + | [9 empty] | © The ARK Electrical Design Co. 2009 | [15 empty] | Tabulated Zs Figures for 5 Second Disconnection Time | [10 empty] | Tabulated Zs Figures for 0.4 Second Disconnection Time
[29 empty] | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
CIRCUIT CALCULATION SHEET: | [8 empty] | CIRCUIT CALCULATION SHEET: | [13 empty] | Short-Circuit Withstand | [7 empty] | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D |  |  | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
Project Name: |  | Fife-JV |  |  |  | Prepared By: | N Holmes |  | Project Name: |  | Fife-JV | [5 empty] | Prepared By: | N Holmes |  |  |  |  | Is Ipsc trip time > 0.1s | [5 empty] | 6A | B | 8 | 7.7 |  |  | 8.8 |  | 7.6 |  |  | 6A | B | 8 | 7.7 |  |  | 8 |  | 7.6
Project Nº: |  | MW502 |  |  |  | Date Prepared: | 08.10.10 |  | Project Nº: |  | MW502 | [5 empty] | Date Prepared: | 08.10.10 |  |  |  |  | If YES, then I²S² from ABB required |  | HOMERUN | EXTENDER | SERVICE DROP |  | " | C | 4 | 3.8 |  |  | 8.8 |  | 4.89 |  |  | " | C | 4 | 3.8 |  |  | 4 |  | 3.88
Area/Zone/Level: |  | Level 01 - DB Zone E5¦1¦BP |  |  |  | Revision: | B |  | Area/Zone/Level: |  | Level 01 - DB Zone E5¦1¦BP | [5 empty] | Revision: | B |  |  |  |  | K²S²>A²s | It (Tab): | 40 | 37 | 28 |  | " | D | 2 | 2.7 |  |  | 8.8 |  | 4.89 |  |  | " | D | 2 | 2.7 |  |  | 1 |  | 2.74
Drawing Nº: |  | CD-MS-XX-L(62)-0-XX-001 Rev B |  |  |  | Checked By: | N Holmes |  | Drawing Nº: |  | CD-MS-XX-L(62)-0-XX-001 Rev B | [5 empty] | Checked By: | N Holmes |  |  |  |  | Establish the typical range of A²s from ABB for the range of Ipsc | [5 empty] | 10A | B | 4.8 | 4.6 |  |  | 5.33 |  | 4.6 |  |  | 10A | B | 4.8 | 4.6 |  |  | 4.8 |  | 4.6
Service: |  | Power |  |  |  |  | UCVD Aug 2009 V4.2 |  | Service: |  | Power | [6 empty] | UCVD Aug 2009 V4.2 | [5 empty] | Voltage Drop (Tab): | 12 | 12 | 19 |  | " | C | 2.4 | 2.2 |  |  | 5.33 |  | 2.95 |  |  | " | C | 2.4 | 2.2 |  |  | 2.4 |  | 2.3
[29 empty] | " | D | 1.2 | 1.6 |  |  | 5.33 |  | 2.95 |  |  | " | D | 1.2 | 1.6 |  |  | 1.2 |  | 1.64
DB Ref: |  | E5¦1¦BP | [6 empty] | DB Ref: |  | E5¦1¦BP | [12 empty] | R@20²C (Tab): | 4.61 | 5.6 | 7.98 |  | 16A | B | 3 | 2.9 |  |  | 3.33 |  | 2.88 |  |  | 16A | B | 3 | 2.9 |  |  | 3 |  | 2.88
MDB Nº: |  | E5¦1¦BP¦05 | [6 empty] | MDB Nº: |  | E5¦1¦BP¦05 | [17 empty] | " | C | 1.5 | 1.4 |  |  | 3.33 |  | 1.84 |  |  | " | C | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
Circuit Ref: |  | E5¦1¦BP¦9L3 | [6 empty] | Circuit Ref: |  | E5¦1¦BP¦9L3 | [12 empty] | Zinst_PHASE: | 6.1368 | 6.9888 | 9.959 |  | " | D | 0.75 | 1 |  |  | 3.33 |  | 1.84 |  |  | " | D | 0.75 | 1 |  |  | 0.75 |  | 1.03
[24 empty] | Zinst_CPC: | 6.1368 | 6.9888 | 9.959 |  | 20A | B | 2.4 | 2.3 |  |  | 2.66 |  | 2.3 |  |  | 20A | B | 2.4 | 2.3 |  |  | 2.4 |  | 2.3
DISTRIBUTION BOARD: |  |  |  |  | HOMERUN CABLE: |  |  |  | CIRCUIT INPUT DATA: | [19 empty] | " | C | 1.2 | 1.2 |  |  | 2.66 |  | 1.47 |  |  | " | C | 1.2 | 1.2 |  |  | 1.2 |  | 1.15
Voltage Drop: |  |  | 0.08 | % | Nº of Circuits per MDB: |  | 9 | [16 empty] | CPD_R_Factor: | 1.3312 | 1.248 | 1.248 |  | " | D | 0.6 | 0.8 |  |  | 2.66 |  | 1.47 |  |  | " | D | 0.6 | 0.8 |  |  | 0.6 |  | 0.82
Actual Voltage: |  |  | 224.02 | V | CSA: |  | 4 | mm² | CABLE | CABLE | LENGTH | LOAD (A) |  |  | VOLTAGE DROP (V) |  | Zs | Ipsc | [10 empty] | 25A | B | 1.8 | 1.8 |  |  | 2.14 |  | 1.84 |  |  | 25A | B | 1.8 | 1.8 |  |  | 1.92 |  | 1.84
Fault Current @ DB (Ipsc): |  |  | 5800 | A | Insulation: |  | XL-LSFZH |  | TYPE | LEG | Metres | Per Leg | Total | Per Leg | Total | % | (W) | (A) |  | Zs | Ipsc | %VoltDrop |  | Ambient T (IEE GN5 Table B1): | 1.04 | 1.04 | 1.04 |  | " | C | 1 | 0.9 |  |  | 2.14 |  | 1.18 |  |  | " | C | 1 | 0.9 |  |  | 0.96 |  | 0.92
External P/E Loop (Ze): |  |  | 0.2 | Ω | Operating Temperature (tp): |  | 90 | °C | Home Run | - | 58 | - | 13.04 | 9.0758 | 9.0758 | 3.95 | 0.91 | 307 |  | 0.91 | 307 | 3.95 |  | Temp Factor F (IEE GN5 Table B2): | 1.28 | 1.2 | 1.2 |  | " | D | 0.46 | 0.7 |  |  | 2.14 |  | 1.18 |  |  | " | D | 0.46 | 0.7 |  |  | 0.48 |  | 0.66
[5 empty] | Rating (It): |  | 40 | A | A | 1 | 8 |  | 13.04 | 1.2518 | 10.3276 | 4.5 | 1.03 | 267.1292 |  | 0.12 | -39.8708 | 0.55 |  | Total Factor: | 1.3312 | 1.248 | 1.248 |  | 32A | B | 1.5 | 1.4 |  |  | 1.66 |  | 1.44 |  |  | 32A | B | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
[5 empty] | Volt Drop (R): |  | 12 | mV/A/m | D | 2 | 3 | 13.0435 | 13.04 | 0.7433 | 11.0709 | 4.82 | 1.08 | 254.7237 |  | 0.05 | -12.4056 | 0.32 | [6 empty] | " | C | 0.75 | 0.7 |  |  | 1.66 |  | 0.92 |  |  | " | C | 0.75 | 0.7 |  |  | 0.75 |  | 0.72
CIRCUIT DESIGN: |  |  |  |  | R @ 20°c: |  | 4.61 | Ω/km |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [6 empty] | " | D | 0.38 | 0.5 |  |  | 1.66 |  | 0.92 |  |  | " | D | 0.38 | 0.5 |  |  | 0.37 |  | 0.51
Nominal Voltage (V): |  |  | 230 | V | Phase-Earth Loop Impedance: |  | 12.28 | Ω/km |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Insulation Working Temp (tp): | 90 | 90 | 90 | °c
Homerun Cable Length: |  |  | 58 | m | Ipsc: |  | 307 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Insulation Final Limit Temp: | 250 | 250 | 250 | °c
Max VD: |  |  | 3.92 | % | I²t or A²s: |  | 500 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Disconnection Time: |  |  | 0.4 | s | K²S²: |  | 327184 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Grouping Factor: | 0.5 | 0 | 1
[5 empty] | K²S²>I²t or A²s: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0.71 | 0.71
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Cg: | 0.5 | 0.71 | 1.71
CIRCUIT PROTECTIVE DEVICE (CPD): | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Rating (In): |  |  | 20 | A | ARMOURED EXTENDER CABLE: | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | It ≥ | 40 | 28.169 | 11.6959 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Type (MCB Only): |  |  | B |  | Nº of Circuits/Cables: |  | 10 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manufacturer: |  |  | ABB |  | CSA: |  | 4 | mm² |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | CPD: | ABB | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tabulated Zs: |  |  | 2.3 | Ω | Insulation: |  | XL-LSFZH | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 5 Sec | 2.3 | [5 empty] | 2.4 | 2.3 | 0 | 0 | 2.66 | 0 | 2.3 | 0 | 0 |  |  | 2.4 | 2.3 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
[5 empty] | Operating Temperature (tp): |  | 90 | °C |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0.4 Sec | 2.3 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Rating (It): |  | 37 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Zs: | 2.3 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Volt Drop (R): |  | 12 | mV/A/m |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | CPD | 2.4 | 2.3 | 0 | 0 | 2.66 | 0 | 2.3 | 0 | 0 |  | CPD | 2.4 | 2.3 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
[5 empty] | R @ 20°c: |  | 5.6 | Ω/km |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail MDB Cg: | ü
[5 empty] | Phase-Earth Loop Impedance: |  | 13.98 | Ω/km |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Cg: |  | ü |  |  |  | ABB | [10 empty] | ABB
[5 empty] | Ipsc Max: |  | 267.1292 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Cg: |  |  | ü
| 0 |  |  |  | Ipsc Min: |  | 254.7237 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail VD: | û | ü | ü
[5 empty] | I²t or A²s Max: |  | 300 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Zs: | ü | û | û |  |  |  | 20A Type C |  | 10A Type C
[5 empty] | I²t or A²s Min: |  | 300 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SWITCH DROP/UN-ARMOURED CABLE: | Pass/Fail Home-Run Ipsc: | ü | [5 empty] | Ipsc | A²s | Ipsc | A²s
[5 empty] | K²S²: |  | 327184 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SERVICE DROP CABLE: | Pass/Fail Extender Max Ipsc: | ü
[5 empty] | K²S²>I²t or A²s Max: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Min Ipsc: | ü |  |  |  |  | 1 | 100 | 70 | 100 | 70
[5 empty] | K²S²>I²t or A²s Min: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Ipsc: | ü |  |  |  |  | 2 | 200 | 300 | 200 | 300
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | 3 | 300 | 500 | 300 | 500
[20 empty] | 1.08 | 254.7237 | 4.82 |  | Supply Voltage Drop: | 0.08% |  |  |  |  | 4 | 400 | 980 | 400 | 980
[5 empty] | SERVICE DROP CABLE: |  |  |  | KEY: | [5 empty] | CIRCUIT CHECK: |  |  | OK | [5 empty] | Supply Voltage Drop: | 5.98 |  |  |  |  | 5 | 500 | 1200 | 500 | 1200
[5 empty] | Nº of Circuits/Cables: |  | 1 |  | A = Armoured Extender Cable | [5 empty] | Homerun Overload Protection: |  |  | ü | [11 empty] | 6 | 600 | 1500 | 600 | 1500
[5 empty] | CSA: |  | 2.5 | mm² | D = Service or Switch Drop | [5 empty] | Extender Overload Protection: |  |  | ü | [11 empty] | 7 | 700 | 2000 | 700 | 2000
[5 empty] | Insulation: |  | LSFZH |  | F = Flying Lead | [5 empty] | SD/RL Overload Protection: |  |  | ü | [11 empty] | 8 | 800 | 2100 | 800 | 2100
[5 empty] | Operating Temperature (tp): |  | 90 | °C | S = Splitter/Tee | [5 empty] | Voltage Drop less than 3.92%: |  |  | û | [11 empty] | 9 | 900 | 2500 | 900 | 2500
[5 empty] | Rating (It): |  | 28 | A | U = Armoured Extender Cable | [5 empty] | Calculated Zs less than Tab Zs: |  |  | ü | [11 empty] | 10 | 1000 | 2800 | 1000 | 2800
[5 empty] | Volt Drop (R): |  | 19 | mV/A/m | [21 empty] | 11 | 2000 | 6000 | 2000 | 6000
[5 empty] | R @ 20°c: |  | 7.98 | Ω/km | [21 empty] | 12 | 3000 | 8400 | 3000 | 8400
| RESULTS SUMMARY |  |  |  | Phase-Earth Loop Impedance: |  | 19.92 | Ω/km | [21 empty] | 13 | 4000 | 10000 | 4000 | 10000
| Load: |  | 13.04 |  | Ipsc: |  | 254.7237 | A | NOTES:
| Length: |  | 69 |  | I²t or A²s: |  | 300 |  | 1. Based upon Ambient Temperature of 30°C.
| Zs: |  | 1.08 |  | K²S²: |  | 127806.25 |  | 2. Zs vaule @ source based upon Transfomrer Supply. | [20 empty] | Home-Run: | 307
| Ipsc: |  | 254.7237 |  | K²S²>I²t or A²s: |  | ü |  | 3. Ipsc vaule @ source based upon Transformer Supply (max figure). | [20 empty] | Extender Max: | 267.1292 |  | Thermal Withstand Model
| Voltage Drop: |  | 11.0709 | [5 empty] | 4. Thermal-Withstand current levels taken at MDB, end of 1st Extender & end of circuit leg. | [20 empty] | Extender Min: | 254.7237
| Final Voltage: |  | 212.9491 | [26 empty] | SD: | 254.7237
[31 empty] | Home-Run |  | Extender Max |  | Extender Min
[30 empty] | 13 | 0 |  | 0 |  | 0
[30 empty] | 12 | 0 |  | 0 |  | 0
[30 empty] | 11 | 0 |  | 0 |  | 0
[30 empty] | 10 | 0 |  | 0 |  | 0
[30 empty] | 9 | 0 |  | 0 |  | 0
[30 empty] | 8 | 0 |  | 0 |  | 0
[30 empty] | 7 | 0 |  | 0 |  | 0
[30 empty] | 6 | 0 |  | 0 |  | 0
[30 empty] | 5 | 0 |  | 0 |  | 0
[30 empty] | 4 | 0 |  | 0 |  | 0
[30 empty] | 3 | 500 |  | 0 |  | 0
[30 empty] | 2 | 0 |  | 300 |  | 300
[30 empty] | 1 | 0 |  | 0 |  | 0
[30 empty] | Value: | 500 |  | 300 |  | 300
Note on J15: Enter nº of circuits at MDB (max = 9). This value MUST include all spare capacity.
Note on J16: Enter: 2.50 4.00 6.00
Note on J17: Enter: XL-LSFZH LSFZH
Note on D30: Enter: B C D
Note on J30: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on D31: Enter: BS7671 ABB Hager Schneider
Note on J31: Enter: 1.50 2.50 4.00
Note on J32: Enter: XL-LSFZH LSFZH
Note on J48: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on J49: Enter: 1.50 2.50 4.00
Note on J50: Enter: XL-LSFZH LSFZH

## 10L3
Modular Systems + | [7 empty] | © The ARK Electrical Design Co. 2009 | Modular Systems + | [9 empty] | © The ARK Electrical Design Co. 2009 | [15 empty] | Tabulated Zs Figures for 5 Second Disconnection Time | [10 empty] | Tabulated Zs Figures for 0.4 Second Disconnection Time
[29 empty] | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
CIRCUIT CALCULATION SHEET: | [8 empty] | CIRCUIT CALCULATION SHEET: | [13 empty] | Short-Circuit Withstand | [7 empty] | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D |  |  | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
Project Name: |  | Fife-JV |  |  |  | Prepared By: | N Holmes |  | Project Name: |  | Fife-JV | [5 empty] | Prepared By: | N Holmes |  |  |  |  | Is Ipsc trip time > 0.1s | [5 empty] | 6A | B | 8 | 7.7 |  |  | 8.8 |  | 7.6 |  |  | 6A | B | 8 | 7.7 |  |  | 8 |  | 7.6
Project Nº: |  | MW502 |  |  |  | Date Prepared: | 08.10.10 |  | Project Nº: |  | MW502 | [5 empty] | Date Prepared: | 08.10.10 |  |  |  |  | If YES, then I²S² from ABB required |  | HOMERUN | EXTENDER | SERVICE DROP |  | " | C | 4 | 3.8 |  |  | 8.8 |  | 4.89 |  |  | " | C | 4 | 3.8 |  |  | 4 |  | 3.88
Area/Zone/Level: |  | Level 01 - DB Zone E5¦1¦BP |  |  |  | Revision: | B |  | Area/Zone/Level: |  | Level 01 - DB Zone E5¦1¦BP | [5 empty] | Revision: | B |  |  |  |  | K²S²>A²s | It (Tab): | 40 | 37 | 28 |  | " | D | 2 | 2.7 |  |  | 8.8 |  | 4.89 |  |  | " | D | 2 | 2.7 |  |  | 1 |  | 2.74
Drawing Nº: |  | CD-MS-XX-L(62)-0-XX-001 Rev B |  |  |  | Checked By: | N Holmes |  | Drawing Nº: |  | CD-MS-XX-L(62)-0-XX-001 Rev B | [5 empty] | Checked By: | N Holmes |  |  |  |  | Establish the typical range of A²s from ABB for the range of Ipsc | [5 empty] | 10A | B | 4.8 | 4.6 |  |  | 5.33 |  | 4.6 |  |  | 10A | B | 4.8 | 4.6 |  |  | 4.8 |  | 4.6
Service: |  | Power |  |  |  |  | UCVD Aug 2009 V4.2 |  | Service: |  | Power | [6 empty] | UCVD Aug 2009 V4.2 | [5 empty] | Voltage Drop (Tab): | 12 | 12 | 19 |  | " | C | 2.4 | 2.2 |  |  | 5.33 |  | 2.95 |  |  | " | C | 2.4 | 2.2 |  |  | 2.4 |  | 2.3
[29 empty] | " | D | 1.2 | 1.6 |  |  | 5.33 |  | 2.95 |  |  | " | D | 1.2 | 1.6 |  |  | 1.2 |  | 1.64
DB Ref: |  | E5¦1¦BP | [6 empty] | DB Ref: |  | E5¦1¦BP | [12 empty] | R@20²C (Tab): | 4.61 | 5.6 | 7.98 |  | 16A | B | 3 | 2.9 |  |  | 3.33 |  | 2.88 |  |  | 16A | B | 3 | 2.9 |  |  | 3 |  | 2.88
MDB Nº: |  | E5¦1¦BP¦05 | [6 empty] | MDB Nº: |  | E5¦1¦BP¦05 | [17 empty] | " | C | 1.5 | 1.4 |  |  | 3.33 |  | 1.84 |  |  | " | C | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
Circuit Ref: |  | E5¦1¦BP¦10L3 | [6 empty] | Circuit Ref: |  | E5¦1¦BP¦10L3 | [12 empty] | Zinst_PHASE: | 6.1368 | 6.9888 | 9.959 |  | " | D | 0.75 | 1 |  |  | 3.33 |  | 1.84 |  |  | " | D | 0.75 | 1 |  |  | 0.75 |  | 1.03
[24 empty] | Zinst_CPC: | 6.1368 | 6.9888 | 9.959 |  | 20A | B | 2.4 | 2.3 |  |  | 2.66 |  | 2.3 |  |  | 20A | B | 2.4 | 2.3 |  |  | 2.4 |  | 2.3
DISTRIBUTION BOARD: |  |  |  |  | HOMERUN CABLE: |  |  |  | CIRCUIT INPUT DATA: | [19 empty] | " | C | 1.2 | 1.2 |  |  | 2.66 |  | 1.47 |  |  | " | C | 1.2 | 1.2 |  |  | 1.2 |  | 1.15
Voltage Drop: |  |  | 0.08 | % | Nº of Circuits per MDB: |  | 9 | [16 empty] | CPD_R_Factor: | 1.3312 | 1.248 | 1.248 |  | " | D | 0.6 | 0.8 |  |  | 2.66 |  | 1.47 |  |  | " | D | 0.6 | 0.8 |  |  | 0.6 |  | 0.82
Actual Voltage: |  |  | 224.02 | V | CSA: |  | 4 | mm² | CABLE | CABLE | LENGTH | LOAD (A) |  |  | VOLTAGE DROP (V) |  | Zs | Ipsc | [10 empty] | 25A | B | 1.8 | 1.8 |  |  | 2.14 |  | 1.84 |  |  | 25A | B | 1.8 | 1.8 |  |  | 1.92 |  | 1.84
Fault Current @ DB (Ipsc): |  |  | 5800 | A | Insulation: |  | XL-LSFZH |  | TYPE | LEG | Metres | Per Leg | Total | Per Leg | Total | % | (W) | (A) |  | Zs | Ipsc | %VoltDrop |  | Ambient T (IEE GN5 Table B1): | 1.04 | 1.04 | 1.04 |  | " | C | 1 | 0.9 |  |  | 2.14 |  | 1.18 |  |  | " | C | 1 | 0.9 |  |  | 0.96 |  | 0.92
External P/E Loop (Ze): |  |  | 0.2 | Ω | Operating Temperature (tp): |  | 90 | °C | Home Run | - | 58 | - | 7.38 | 5.1365 | 5.1365 | 2.24 | 0.91 | 307 |  | 0.91 | 307 | 2.24 |  | Temp Factor F (IEE GN5 Table B2): | 1.28 | 1.2 | 1.2 |  | " | D | 0.46 | 0.7 |  |  | 2.14 |  | 1.18 |  |  | " | D | 0.46 | 0.7 |  |  | 0.48 |  | 0.66
[5 empty] | Rating (It): |  | 40 | A | A | 1 | 5 | 1.3043 | 7.38 | 0.4428 | 5.5793 | 2.43 | 0.98 | 280.805 |  | 0.07 | -26.195 | 0.19 |  | Total Factor: | 1.3312 | 1.248 | 1.248 |  | 32A | B | 1.5 | 1.4 |  |  | 1.66 |  | 1.44 |  |  | 32A | B | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
[5 empty] | Volt Drop (R): |  | 12 | mV/A/m | A | 2 | 4 | 4.7826 | 6.08 | 0.2918 | 5.8711 | 2.56 | 1.04 | 262.8619 |  | 0.06 | -17.9431 | 0.13 | [6 empty] | " | C | 0.75 | 0.7 |  |  | 1.66 |  | 0.92 |  |  | " | C | 0.75 | 0.7 |  |  | 0.75 |  | 0.72
CIRCUIT DESIGN: |  |  |  |  | R @ 20°c: |  | 4.61 | Ω/km | A | 3 | 2 |  | 1.3 | 0.0312 | 5.9023 | 2.57 | 1.07 | 254.7237 |  | 0.03 | -8.1383 | 0.01 | [6 empty] | " | D | 0.38 | 0.5 |  |  | 1.66 |  | 0.92 |  |  | " | D | 0.38 | 0.5 |  |  | 0.37 |  | 0.51
Nominal Voltage (V): |  |  | 230 | V | Phase-Earth Loop Impedance: |  | 12.28 | Ω/km | D | 4 | 3 | 1.3043 | 1.3 | 0.0741 | 5.9764 | 2.6 | 1.12 | 243.4192 |  | 0.05 | -11.3045 | 0.03 |  | Insulation Working Temp (tp): | 90 | 90 | 90 | °c
Homerun Cable Length: |  |  | 58 | m | Ipsc: |  | 307 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Insulation Final Limit Temp: | 250 | 250 | 250 | °c
Max VD: |  |  | 3.92 | % | I²t or A²s: |  | 500 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Disconnection Time: |  |  | 0.4 | s | K²S²: |  | 327184 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Grouping Factor: | 0.5 | 0 | 1
[5 empty] | K²S²>I²t or A²s: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0.71 | 0.71
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Cg: | 0.5 | 0.71 | 1.71
CIRCUIT PROTECTIVE DEVICE (CPD): | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Rating (In): |  |  | 20 | A | ARMOURED EXTENDER CABLE: | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | It ≥ | 40 | 28.169 | 11.6959 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Type (MCB Only): |  |  | B |  | Nº of Circuits/Cables: |  | 10 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manufacturer: |  |  | ABB |  | CSA: |  | 4 | mm² |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | CPD: | ABB | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tabulated Zs: |  |  | 2.3 | Ω | Insulation: |  | XL-LSFZH | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 5 Sec | 2.3 | [5 empty] | 2.4 | 2.3 | 0 | 0 | 2.66 | 0 | 2.3 | 0 | 0 |  |  | 2.4 | 2.3 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
[5 empty] | Operating Temperature (tp): |  | 90 | °C |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0.4 Sec | 2.3 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Rating (It): |  | 37 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Zs: | 2.3 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Volt Drop (R): |  | 12 | mV/A/m |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | CPD | 2.4 | 2.3 | 0 | 0 | 2.66 | 0 | 2.3 | 0 | 0 |  | CPD | 2.4 | 2.3 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
[5 empty] | R @ 20°c: |  | 5.6 | Ω/km |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail MDB Cg: | ü
[5 empty] | Phase-Earth Loop Impedance: |  | 13.98 | Ω/km |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Cg: |  | ü |  |  |  | ABB | [10 empty] | ABB
[5 empty] | Ipsc Max: |  | 280.805 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Cg: |  |  | ü
| 0 |  |  |  | Ipsc Min: |  | 243.4192 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail VD: | ü | ü | ü
[5 empty] | I²t or A²s Max: |  | 300 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Zs: | ü | û | û |  |  |  | 20A Type C |  | 10A Type C
[5 empty] | I²t or A²s Min: |  | 300 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SWITCH DROP/UN-ARMOURED CABLE: | Pass/Fail Home-Run Ipsc: | ü | [5 empty] | Ipsc | A²s | Ipsc | A²s
[5 empty] | K²S²: |  | 327184 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SERVICE DROP CABLE: | Pass/Fail Extender Max Ipsc: | ü
[5 empty] | K²S²>I²t or A²s Max: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Min Ipsc: | ü |  |  |  |  | 1 | 100 | 70 | 100 | 70
[5 empty] | K²S²>I²t or A²s Min: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Ipsc: | ü |  |  |  |  | 2 | 200 | 300 | 200 | 300
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | 3 | 300 | 500 | 300 | 500
[20 empty] | 1.12 | 243.4192 | 2.6 |  | Supply Voltage Drop: | 0.08% |  |  |  |  | 4 | 400 | 980 | 400 | 980
[5 empty] | SERVICE DROP CABLE: |  |  |  | KEY: | [5 empty] | CIRCUIT CHECK: |  |  | OK | [5 empty] | Supply Voltage Drop: | 5.98 |  |  |  |  | 5 | 500 | 1200 | 500 | 1200
[5 empty] | Nº of Circuits/Cables: |  | 1 |  | A = Armoured Extender Cable | [5 empty] | Homerun Overload Protection: |  |  | ü | [11 empty] | 6 | 600 | 1500 | 600 | 1500
[5 empty] | CSA: |  | 2.5 | mm² | D = Service or Switch Drop | [5 empty] | Extender Overload Protection: |  |  | ü | [11 empty] | 7 | 700 | 2000 | 700 | 2000
[5 empty] | Insulation: |  | LSFZH |  | F = Flying Lead | [5 empty] | SD/RL Overload Protection: |  |  | ü | [11 empty] | 8 | 800 | 2100 | 800 | 2100
[5 empty] | Operating Temperature (tp): |  | 90 | °C | S = Splitter/Tee | [5 empty] | Voltage Drop less than 3.92%: |  |  | ü | [11 empty] | 9 | 900 | 2500 | 900 | 2500
[5 empty] | Rating (It): |  | 28 | A | U = Armoured Extender Cable | [5 empty] | Calculated Zs less than Tab Zs: |  |  | ü | [11 empty] | 10 | 1000 | 2800 | 1000 | 2800
[5 empty] | Volt Drop (R): |  | 19 | mV/A/m | [21 empty] | 11 | 2000 | 6000 | 2000 | 6000
[5 empty] | R @ 20°c: |  | 7.98 | Ω/km | [21 empty] | 12 | 3000 | 8400 | 3000 | 8400
| RESULTS SUMMARY |  |  |  | Phase-Earth Loop Impedance: |  | 19.92 | Ω/km | [21 empty] | 13 | 4000 | 10000 | 4000 | 10000
| Load: |  | 7.38 |  | Ipsc: |  | 243.4192 | A | NOTES:
| Length: |  | 72 |  | I²t or A²s: |  | 300 |  | 1. Based upon Ambient Temperature of 30°C.
| Zs: |  | 1.12 |  | K²S²: |  | 127806.25 |  | 2. Zs vaule @ source based upon Transfomrer Supply. | [20 empty] | Home-Run: | 307
| Ipsc: |  | 243.4192 |  | K²S²>I²t or A²s: |  | ü |  | 3. Ipsc vaule @ source based upon Transformer Supply (max figure). | [20 empty] | Extender Max: | 280.805 |  | Thermal Withstand Model
| Voltage Drop: |  | 5.9764 | [5 empty] | 4. Thermal-Withstand current levels taken at MDB, end of 1st Extender & end of circuit leg. | [20 empty] | Extender Min: | 243.4192
| Final Voltage: |  | 218.0436 | [26 empty] | SD: | 243.4192
[31 empty] | Home-Run |  | Extender Max |  | Extender Min
[30 empty] | 13 | 0 |  | 0 |  | 0
[30 empty] | 12 | 0 |  | 0 |  | 0
[30 empty] | 11 | 0 |  | 0 |  | 0
[30 empty] | 10 | 0 |  | 0 |  | 0
[30 empty] | 9 | 0 |  | 0 |  | 0
[30 empty] | 8 | 0 |  | 0 |  | 0
[30 empty] | 7 | 0 |  | 0 |  | 0
[30 empty] | 6 | 0 |  | 0 |  | 0
[30 empty] | 5 | 0 |  | 0 |  | 0
[30 empty] | 4 | 0 |  | 0 |  | 0
[30 empty] | 3 | 500 |  | 0 |  | 0
[30 empty] | 2 | 0 |  | 300 |  | 300
[30 empty] | 1 | 0 |  | 0 |  | 0
[30 empty] | Value: | 500 |  | 300 |  | 300
Note on J15: Enter nº of circuits at MDB (max = 9). This value MUST include all spare capacity.
Note on J16: Enter: 2.50 4.00 6.00
Note on J17: Enter: XL-LSFZH LSFZH
Note on D30: Enter: B C D
Note on J30: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on D31: Enter: BS7671 ABB Hager Schneider
Note on J31: Enter: 1.50 2.50 4.00
Note on J32: Enter: XL-LSFZH LSFZH
Note on J48: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on J49: Enter: 1.50 2.50 4.00
Note on J50: Enter: XL-LSFZH LSFZH