## Index
The ARK Electrical Design Co.
Fife New Hospital Joint Venture
Cable Calculation Index
Project Name: |  | Fife-JV |  |  |  | Date: | 26.06.10
Project Nº: |  | MW502 |  |  |  | By: | N Holmes
Area/Zone/Level: |  | Level 00 - DB Zone E1¦0¦BL
Drawing Nº: |  | CD-MS-02-L(62)1-XX-006
Service: |  | Lighting
Nominal Voltage: |  | 230
Max Volt Drop: |  | 4%
Distribution Board Data |  |  | L1 | L2 | L3
DB Ref: |  | 2
Voltage Drop: |  |  | 2.15% | 2.15% | 2.15%
Final Voltage: |  |  | 229.5055 | 229.5055 | 229.5055
Ipsc (Max): |  | 14430
Ipsc (Min): |  | 1500
Zs: |  | 0.07373
| MDB Nº |  | Circuit Ref |  |  | Legs
| L01 |  | 1L1 |  |  | a
| L02 |  | 5L1 |  |  | a
| L02 |  | 5L2
| L03 |  | 7L3 |  |  | a - b
Notes:
1. | Where conntection points/outlets are located within the Ceiling Void (CV), no Service Drop (SD) is shown.

## Luminaire Schedule
Modular Systems + | [6 empty] | The ARK Electrical Design Co.
Fife New Hospital-Joint Venture
Luminaire Schedule |  |  |  |  | Date: | 26.06.10
Project Name: |  | Fife-JV |  |  | By: | N Holmes
Project Nº: |  | MW502
Area/Zone/Level: |  | Level 00 - DB Zone E1¦0¦BL
Drawing Nº: |  | CD-MS-02-L(62)1-XX-006
Service: |  | Lighting
Ref | Lamp Rating | QTY Lamps | Total Load | Ref | Lamp Rating | QTY Lamps | Total Load
A | 54 | 2+1 | 118 | T | 24 | 4 | 102
B | 54 | 1 | 61 | U
C | 26 | 2 | 54 | V | 58 | 2 | 163
C2 | 18 | 1 | 19 | W | 54 | 1 | 61
C3 | 18 | 2 | 38 | W1 | 54 | 1 | 61
D | 14 | 4 | 62 | W2 | 24 | 3 | 79
EM | 8 | 1 | 8 | W3 | 36 | 2 | 72
EX | 8 | 1 | 8 | Y | 70 | 1 | 80
F | 26 | 2 | 52 | Y2 | 12 | 1 | 16
G | 14 | 4 | 62
H1 | 54 | 4 | 236 | EX2 | 100 | 1 | 100
H2 | 54 | 4 | 236
J | 14 | 4 | 62
K | 26 | 2 | 54
L | 54 | 1 | 61
M | 54 | 1 | 61
M2 | 54 | 2 | 118
N | 55 | 4 | 232
P | 24 | 4 | 102
P1 | 14 | 4 | 62
Q | 49 | 2 | 109
Q2 | 36 | 2 | 72
R | 55 | 1 | 58
S | 14 | 4 | 62 |  | 50 | 1 | 20

## 14L1
[8 empty] | © The ARK Electrical Design Co. | [10 empty] | © The ARK Electrical Design Co. | [15 empty] | Tabulated Zs Figures for 5 Second Disconnection Time | [10 empty] | Tabulated Zs Figures for 0.4 Second Disconnection Time
[29 empty] | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
CIRCUIT CALCULATION SHEET: | [8 empty] | CIRCUIT CALCULATION SHEET: | [13 empty] | Short-Circuit Withstand | [7 empty] | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D |  |  | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
Project Name: |  | Fife-JV |  |  |  | Prepared By: | N Holmes |  | Project Name: |  | Fife-JV | [5 empty] | Prepared By: | N Holmes |  |  |  |  | Is Ipsc trip time > 0.1s | [5 empty] | 6A | B | 8 | 7.7 |  |  | 8.8 |  | 7.6 |  |  | 6A | B | 8 | 7.7 |  |  | 8 |  | 7.6
Project Nº: |  | MW502 |  |  |  | Date Prepared: | 26.06.10 |  | Project Nº: |  | MW502 | [5 empty] | Date Prepared: | 26.06.10 |  |  |  |  | If YES, then I²S² from ABB required |  | FEEDER | FLAT WIRING | FLYING LEAD |  | " | C | 4 | 3.8 |  |  | 8.8 |  | 4.89 |  |  | " | C | 4 | 3.8 |  |  | 4 |  | 3.88
Area/Zone/Level: |  | Level 00 - DB Zone E1¦0¦BL |  |  |  | Revision: | C1 |  | Area/Zone/Level: |  | Level 00 - DB Zone E1¦0¦BL | [5 empty] | Revision: | C1 |  |  |  |  | K²S²>A²s | It (Tab): | 34 | 30 | 16 |  | " | D | 2 | 2.7 |  |  | 8.8 |  | 4.89 |  |  | " | D | 2 | 2.7 |  |  | 1 |  | 2.74
Drawing Nº: |  | CD-MS-02-L(62)1-XX-006 |  |  |  | Checked By: |  |  | Drawing Nº: |  | CD-MS-02-L(62)1-XX-006 | [5 empty] | Checked By: | 0 |  |  |  |  | Establish the typical range of A²s from ABB for the range of Ipsc | [5 empty] | 10A | B | 4.8 | 4.6 |  |  | 5.33 |  | 4.6 |  |  | 10A | B | 4.8 | 4.6 |  |  | 4.8 |  | 4.6
Service: |  | Lighting |  |  |  |  | UCVD May 2010 V4.3 |  | Service: |  | Lighting | [6 empty] | UCVD May 2010 V4.3 | [5 empty] | Voltage Drop (Tab): | 12 | 18 | 32 |  | " | C | 2.4 | 2.2 |  |  | 5.33 |  | 2.95 |  |  | " | C | 2.4 | 2.2 |  |  | 2.4 |  | 2.3
[29 empty] | " | D | 1.2 | 1.6 |  |  | 5.33 |  | 2.95 |  |  | " | D | 1.2 | 1.6 |  |  | 1.2 |  | 1.64
DB Ref: |  | 2 | [6 empty] | DB Ref: |  | 2 | [12 empty] | R@20²C (Tab): | 4.95 | 7.98 | 13.3 |  | 16A | B | 3 | 2.9 |  |  | 3.33 |  | 2.88 |  |  | 16A | B | 3 | 2.9 |  |  | 3 |  | 2.88
[9 empty] | 0 |  | 0 | [17 empty] | " | C | 1.5 | 1.4 |  |  | 3.33 |  | 1.84 |  |  | " | C | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
Circuit Ref: |  | 2¦14L1 | [6 empty] | Circuit Ref: |  | 2¦14L1 | [12 empty] | Zinst_PHASE: | 6.1776 | 9.959 | 16.5984 |  | " | D | 0.75 | 1 |  |  | 3.33 |  | 1.84 |  |  | " | D | 0.75 | 1 |  |  | 0.75 |  | 1.03
[24 empty] | Zinst_CPC: | 6.1776 | 9.959 | 16.5984 |  | 20A | B | 2.4 | 2.3 |  |  | 2.66 |  | 2.3 |  |  | 20A | B | 2.4 | 2.3 |  |  | 2.4 |  | 2.3
DISTRIBUTION BOARD: |  |  |  |  | FEEDER CABLE: |  |  |  | CIRCUIT INPUT DATA: | [19 empty] | " | C | 1.2 | 1.2 |  |  | 2.66 |  | 1.47 |  |  | " | C | 1.2 | 1.2 |  |  | 1.2 |  | 1.15
Voltage Drop: |  |  | 2.15 | % | Nº of Circuits per MDB: |  | 12 | [16 empty] | CPD_R_Factor: | 1.248 | 1.248 | 1.248 |  | " | D | 0.6 | 0.8 |  |  | 2.66 |  | 1.47 |  |  | " | D | 0.6 | 0.8 |  |  | 0.6 |  | 0.82
Actual Voltage: |  |  | 225.055 | V | CSA: |  | 4 | mm² | CABLE | CABLE | LENGTH | LOAD (A) |  |  | VOLTAGE DROP (V) |  | Zs | Ipsc | [10 empty] | 25A | B | 1.8 | 1.8 |  |  | 2.14 |  | 1.84 |  |  | 25A | B | 1.8 | 1.8 |  |  | 1.92 |  | 1.84
Fault Current @ DB (Ipsc): |  |  | 14430 | A | Insulation: |  | LSFZH |  | TYPE | LEG | Metres | Per Leg | Total | Per Leg | Total | % | (W) | (A) |  | Zs | Ipsc | %VoltDrop |  | Ambient T (IEE GN5 Table B1): | 1.04 | 1.04 | 1.04 |  | " | C | 1 | 0.9 |  |  | 2.14 |  | 1.18 |  |  | " | C | 1 | 0.9 |  |  | 0.96 |  | 0.92
External P/E Loop (Ze): |  |  | 0.07373 | Ω | Operating Temperature (tp): |  | 70 | °C | Feeder | - | 25 | - | 4.24 | 1.272 | 1.272 | 0.56 | 0.38 | 709 |  | 0.38 | 709 | 0.56 |  | Temp Factor F (IEE GN5 Table B2): | 1.2 | 1.2 | 1.2 |  | " | D | 0.46 | 0.7 |  |  | 2.14 |  | 1.18 |  |  | " | D | 0.46 | 0.7 |  |  | 0.48 |  | 0.66
[5 empty] | Rating (It): |  | 34 | A | FW | 1 | 0 | 0.94783 | 4.24 | 0 | 1.272 | 0.56 | 0.38 | 709 |  | 0 | 0 | 0 |  | Total Factor: | 1.248 | 1.248 | 1.248 |  | 32A | B | 1.5 | 1.4 |  |  | 1.66 |  | 1.44 |  |  | 32A | B | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
[5 empty] | Volt Drop (R): |  | 12 | mV/A/m | FW | 2 | 1.7 | 0.47391 | 3.29 | 0.1007 | 1.3727 | 0.6 | 0.42 | 641.9895 |  | 0.04 | -67.0105 | 0.04 | [6 empty] | " | C | 0.75 | 0.7 |  |  | 1.66 |  | 0.92 |  |  | " | C | 0.75 | 0.7 |  |  | 0.75 |  | 0.72
CIRCUIT DESIGN: |  |  |  |  | R @ 20°c: |  | 4.95 | Ω/kM | FW | 3 | 3.7 | 0.47391 | 2.82 | 0.1878 | 1.5605 | 0.68 | 0.5 | 532.4589 |  | 0.08 | -109.5306 | 0.08 | [6 empty] | " | D | 0.38 | 0.5 |  |  | 1.66 |  | 0.92 |  |  | " | D | 0.38 | 0.5 |  |  | 0.37 |  | 0.51
Nominal Voltage (V): |  |  | 230 | V | Phase-Earth Loop Impedance: |  | 12.36 | Ω/kM | FW | 4 | 3.7 | 0.47391 | 2.35 | 0.1565 | 1.717 | 0.75 | 0.58 | 454.8555 |  | 0.08 | -77.6034 | 0.07 |  | Insulation Working Temp (tp): | 70 | 70 | 70 | °c
Homerun Cable Length: |  |  | 25 | m | Ipsc: |  | 709 | A | FW | 5 | 3.7 | 0.47391 | 1.88 | 0.1252 | 1.8422 | 0.81 | 0.66 | 396.9953 |  | 0.08 | -57.8602 | 0.06 |  | Insulation Final Limit Temp: | 160 | 160 | 160 | °c
Max VD: |  |  | 1.85 | % | I²t or A²s: |  | 2000 |  | FW | 6 | 1.9 | 0.47391 | 1.41 | 0.0482 | 1.8904 | 0.83 | 0.7 | 372.6529 |  | 0.04 | -24.3424 | 0.02
Disconnection Time: |  |  | 0.4 | s | K²S²: |  | 327184 |  | FW | 7 | 1.8 | 0.47391 | 0.94 | 0.0305 | 1.9209 | 0.84 | 0.74 | 352.1942 |  | 0.04 | -20.4587 | 0.01 |  | Grouping Factor: | 0 | 1 | 1
[5 empty] | K²S²>I²t or A²s: |  | ü |  | FW | 8 | 3.7 |  | 0.47 | 0.0313 | 1.9522 | 0.85 | 0.82 | 316.4793 |  | 0.08 | -35.7148 | 0.01 |  |  | 0.7 | 0 | 0
[9 empty] | FL | 9 | 1 | 0.47391 | 0.47 | 0.015 | 1.9672 | 0.86 | 0.84 | 308.0369 |  | 0.02 | -8.4424 | 0.01 |  | Cg: | 0.7 | 1 | 1
CIRCUIT PROTECTIVE DEVICE (CPD): | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Rating (In): |  |  | 10 | A | FLAT WIRING | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | It ≥ | 14.2857 | 10 | 10 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Type (MCB Only): |  |  | C |  | Nº of Circuits/Cables: |  | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [8 empty] | 2.4 | 2.2 | 0 | 0 | 5.33 | 0 | 2.95 | 0 | 0 |  |  | 2.4 | 2.2 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
Manufacturer: |  |  | Schneider |  | CSA: |  | 2.5 | mm² |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | CPD: | Schneider | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tabulated Zs: |  |  | 2.4 | Ω | Insulation: |  | LSFZH | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 5 Sec | 2.95 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Operating Temperature (tp): |  | 70 | °C |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0.4 Sec | 2.4 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Rating (It): |  | 30 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Zs: | 2.4 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Volt Drop (R): |  | 18 | mV/A/m |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | CPD | 2.4 | 2.2 | 0 | 0 | 5.33 | 0 | 2.95 | 0 | 0 |  | CPD | 2.4 | 2.2 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
[5 empty] | R @ 20°c: |  | 7.98 | Ω/kM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail MDB Cg: | ü
[5 empty] | Phase-Earth Loop Impedance: |  | 19.92 | Ω/kM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Cg: |  | ü |  |  |  | Schneider | [10 empty] | Schneider
[5 empty] | Ipsc Max: |  | 709 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Cg: |  |  | ü
| This calculation is un-checked |  |  |  | Ipsc Min: |  | 308.0369 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail VD: | ü | ü | ü
[5 empty] | I²t or A²s Max: |  | 2000 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Zs: | ü | û | û |  |  |  | 20A Type C |  | 10A Type C
[5 empty] | I²t or A²s Min: |  | 500 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SWITCH DROP/UN-ARMOURED CABLE: | Pass/Fail Home-Run Ipsc: | ü | [5 empty] | Ipsc | A²s | Ipsc | A²s
[5 empty] | K²S²: |  | 127806.25 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SERVICE DROP CABLE: | Pass/Fail Extender Max Ipsc: | ü
[5 empty] | K²S²>I²t or A²s Max: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Min Ipsc: | ü |  |  |  |  | 1 | 100 | 70 | 100 | 70
[5 empty] | K²S²>I²t or A²s Min: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Ipsc: | ü |  |  |  |  | 2 | 200 | 300 | 200 | 300
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | 3 | 300 | 500 | 300 | 500
[20 empty] | 0.84 | 308.0369 | 0.86 |  | Supply Voltage Drop: | 2.15% |  |  |  |  | 4 | 400 | 980 | 400 | 980
[5 empty] | FLYING LEAD |  |  |  | KEY: | [5 empty] | CIRCUIT CHECK: |  |  | OK | [5 empty] | Supply Voltage Drop: | 4.945 |  |  |  |  | 5 | 500 | 1200 | 500 | 1200
[5 empty] | Nº of Circuits/Cables: |  | 1 |  | FW = Flat Wiring | [5 empty] | Homerun Overload Protection: |  |  | ü | [5 empty] | Supply Voltage: | 229.5055 |  |  |  |  | 6 | 600 | 1500 | 600 | 1500
[5 empty] | CSA: |  | 1.5 | mm² | FL = Flying Lead | [5 empty] | Extender Overload Protection: |  |  | ü | [11 empty] | 7 | 700 | 2000 | 700 | 2000
[5 empty] | Insulation: |  | LSFZH | [7 empty] | SD/RL Overload Protection: |  |  | ü | [11 empty] | 8 | 800 | 2100 | 800 | 2100
[5 empty] | Operating Temperature (tp): |  | 70 | °C | [6 empty] | Voltage Drop less than 1.85%: |  |  | ü | [11 empty] | 9 | 900 | 2500 | 900 | 2500
[5 empty] | Rating (It): |  | 16 | A | [6 empty] | Calculated Zs less than Tab Zs: |  |  | ü | [11 empty] | 10 | 1000 | 2800 | 1000 | 2800
[5 empty] | Volt Drop (R): |  | 32 | mV/A/m | [21 empty] | 11 | 2000 | 6000 | 2000 | 6000
[5 empty] | R @ 20°c: |  | 13.3 | Ω/kM | [21 empty] | 12 | 3000 | 8400 | 3000 | 8400
| RESULTS SUMMARY |  |  |  | Phase-Earth Loop Impedance: |  | 33.2 | Ω/kM | [21 empty] | 13 | 4000 | 10000 | 4000 | 10000
| Load: |  | 4.24 |  | Ipsc: |  | 308.0369 | A | NOTES:
| Length: |  | 46.2 |  | I²t or A²s: |  | 500 |  | 1. Based upon Ambient Temperature of 30°C.
| Zs: |  | 0.84 |  | K²S²: |  | 46010.25 |  | 2. Zs vaule @ source based upon Transfomrer Supply. | [20 empty] | Home-Run: | 709
| Ipsc: |  | 308.0369 |  | K²S²>I²t or A²s: |  | ü |  | 3. Ipsc vaule @ source based upon Transformer Supply (max figure). | [20 empty] | Extender Max: | 709 |  | Thermal Withstand Model
| Voltage Drop: |  | 1.9672 | [5 empty] | 4. Thermal-Withstand current levels taken at MDB, end of 1st Extender & end of circuit leg. | [20 empty] | Extender Min: | 308.0369
| Final Voltage: |  | 223.0878 | [26 empty] | SD: | 308.0369
[31 empty] | Home-Run |  | Extender Max |  | Extender Min
[30 empty] | 13 | 0 |  | 0 |  | 0
[30 empty] | 12 | 0 |  | 0 |  | 0
[30 empty] | 11 | 0 |  | 0 |  | 0
[30 empty] | 10 | 0 |  | 0 |  | 0
[30 empty] | 9 | 0 |  | 0 |  | 0
[30 empty] | 8 | 0 |  | 0 |  | 0
[30 empty] | 7 | 2000 |  | 2000 |  | 0
[30 empty] | 6 | 0 |  | 0 |  | 0
[30 empty] | 5 | 0 |  | 0 |  | 0
[30 empty] | 4 | 0 |  | 0 |  | 0
[30 empty] | 3 | 0 |  | 0 |  | 500
[30 empty] | 2 | 0 |  | 0 |  | 0
[30 empty] | 1 | 0 |  | 0 |  | 0
[30 empty] | Value: | 2000 |  | 2000 |  | 500
Note on J15: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on J16: Enter: 2.50 4.00 6.00
Note on J17: Enter: XL-LSFZH LSFZH
Note on D30: Enter: B C D
Note on J30: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on D31: Enter: BS7671 ABB Hager Schneider
Note on J31: Enter: 1.50 2.50 4.00
Note on J32: Enter: XL-LSFZH LSFZH
Note on J48: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on J49: Enter: 1.50 2.50 4.00
Note on J50: Enter: XL-LSFZH LSFZH

## 14L2
[8 empty] | © The ARK Electrical Design Co. | [10 empty] | © The ARK Electrical Design Co. | [15 empty] | Tabulated Zs Figures for 5 Second Disconnection Time | [10 empty] | Tabulated Zs Figures for 0.4 Second Disconnection Time
[29 empty] | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
CIRCUIT CALCULATION SHEET: | [8 empty] | CIRCUIT CALCULATION SHEET: | [13 empty] | Short-Circuit Withstand | [7 empty] | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D |  |  | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
Project Name: |  | Fife-JV |  |  |  | Prepared By: | N Holmes |  | Project Name: |  | Fife-JV | [5 empty] | Prepared By: | N Holmes |  |  |  |  | Is Ipsc trip time > 0.1s | [5 empty] | 6A | B | 8 | 7.7 |  |  | 8.8 |  | 7.6 |  |  | 6A | B | 8 | 7.7 |  |  | 8 |  | 7.6
Project Nº: |  | MW502 |  |  |  | Date Prepared: | 26.06.10 |  | Project Nº: |  | MW502 | [5 empty] | Date Prepared: | 26.06.10 |  |  |  |  | If YES, then I²S² from ABB required |  | FEEDER | FLAT WIRING | FLYING LEAD |  | " | C | 4 | 3.8 |  |  | 8.8 |  | 4.89 |  |  | " | C | 4 | 3.8 |  |  | 4 |  | 3.88
Area/Zone/Level: |  | Level 00 - DB Zone E1¦0¦BL |  |  |  | Revision: | C1 |  | Area/Zone/Level: |  | Level 00 - DB Zone E1¦0¦BL | [5 empty] | Revision: | C1 |  |  |  |  | K²S²>A²s | It (Tab): | 34 | 30 | 16 |  | " | D | 2 | 2.7 |  |  | 8.8 |  | 4.89 |  |  | " | D | 2 | 2.7 |  |  | 1 |  | 2.74
Drawing Nº: |  | CD-MS-02-L(62)1-XX-006 |  |  |  | Checked By: |  |  | Drawing Nº: |  | CD-MS-02-L(62)1-XX-006 | [5 empty] | Checked By: | 0 |  |  |  |  | Establish the typical range of A²s from ABB for the range of Ipsc | [5 empty] | 10A | B | 4.8 | 4.6 |  |  | 5.33 |  | 4.6 |  |  | 10A | B | 4.8 | 4.6 |  |  | 4.8 |  | 4.6
Service: |  | Lighting |  |  |  |  | UCVD May 2010 V4.3 |  | Service: |  | Lighting | [6 empty] | UCVD May 2010 V4.3 | [5 empty] | Voltage Drop (Tab): | 12 | 18 | 32 |  | " | C | 2.4 | 2.2 |  |  | 5.33 |  | 2.95 |  |  | " | C | 2.4 | 2.2 |  |  | 2.4 |  | 2.3
[29 empty] | " | D | 1.2 | 1.6 |  |  | 5.33 |  | 2.95 |  |  | " | D | 1.2 | 1.6 |  |  | 1.2 |  | 1.64
DB Ref: |  | 2 | [6 empty] | DB Ref: |  | 2 | [12 empty] | R@20²C (Tab): | 4.95 | 7.98 | 13.3 |  | 16A | B | 3 | 2.9 |  |  | 3.33 |  | 2.88 |  |  | 16A | B | 3 | 2.9 |  |  | 3 |  | 2.88
[9 empty] | 0 |  | 0 | [17 empty] | " | C | 1.5 | 1.4 |  |  | 3.33 |  | 1.84 |  |  | " | C | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
Circuit Ref: |  | 2¦14L2 | [6 empty] | Circuit Ref: |  | 2¦14L2 | [12 empty] | Zinst_PHASE: | 6.1776 | 9.959 | 16.5984 |  | " | D | 0.75 | 1 |  |  | 3.33 |  | 1.84 |  |  | " | D | 0.75 | 1 |  |  | 0.75 |  | 1.03
[24 empty] | Zinst_CPC: | 6.1776 | 9.959 | 16.5984 |  | 20A | B | 2.4 | 2.3 |  |  | 2.66 |  | 2.3 |  |  | 20A | B | 2.4 | 2.3 |  |  | 2.4 |  | 2.3
DISTRIBUTION BOARD: |  |  |  |  | FEEDER CABLE: |  |  |  | CIRCUIT INPUT DATA: | [19 empty] | " | C | 1.2 | 1.2 |  |  | 2.66 |  | 1.47 |  |  | " | C | 1.2 | 1.2 |  |  | 1.2 |  | 1.15
Voltage Drop: |  |  | 2.15 | % | Nº of Circuits per MDB: |  | 12 | [16 empty] | CPD_R_Factor: | 1.248 | 1.248 | 1.248 |  | " | D | 0.6 | 0.8 |  |  | 2.66 |  | 1.47 |  |  | " | D | 0.6 | 0.8 |  |  | 0.6 |  | 0.82
Actual Voltage: |  |  | 225.055 | V | CSA: |  | 4 | mm² | CABLE | CABLE | LENGTH | LOAD (A) |  |  | VOLTAGE DROP (V) |  | Zs | Ipsc | [10 empty] | 25A | B | 1.8 | 1.8 |  |  | 2.14 |  | 1.84 |  |  | 25A | B | 1.8 | 1.8 |  |  | 1.92 |  | 1.84
Fault Current @ DB (Ipsc): |  |  | 14430 | A | Insulation: |  | LSFZH |  | TYPE | LEG | Metres | Per Leg | Total | Per Leg | Total | % | (W) | (A) |  | Zs | Ipsc | %VoltDrop |  | Ambient T (IEE GN5 Table B1): | 1.04 | 1.04 | 1.04 |  | " | C | 1 | 0.9 |  |  | 2.14 |  | 1.18 |  |  | " | C | 1 | 0.9 |  |  | 0.96 |  | 0.92
External P/E Loop (Ze): |  |  | 0.07373 | Ω | Operating Temperature (tp): |  | 70 | °C | Feeder | - | 22 | - | 7.56 | 1.9958 | 1.9958 | 0.87 | 0.35 | 800 |  | 0.35 | 800 | 0.87 |  | Temp Factor F (IEE GN5 Table B2): | 1.2 | 1.2 | 1.2 |  | " | D | 0.46 | 0.7 |  |  | 2.14 |  | 1.18 |  |  | " | D | 0.46 | 0.7 |  |  | 0.48 |  | 0.66
[5 empty] | Rating (It): |  | 34 | A | FW | 1 | 0 | 2.3696 | 7.56 | 0 | 1.9958 | 0.87 | 0.35 | 800 |  | 0 | 1.1369e-13 | 0 |  | Total Factor: | 1.248 | 1.248 | 1.248 |  | 32A | B | 1.5 | 1.4 |  |  | 1.66 |  | 1.44 |  |  | 32A | B | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
[5 empty] | Volt Drop (R): |  | 12 | mV/A/m | FW | 2 | 1.7 | 0.47391 | 5.19 | 0.1588 | 2.1546 | 0.94 | 0.39 | 715.7066 |  | 0.04 | -84.2934 | 0.07 | [6 empty] | " | C | 0.75 | 0.7 |  |  | 1.66 |  | 0.92 |  |  | " | C | 0.75 | 0.7 |  |  | 0.75 |  | 0.72
CIRCUIT DESIGN: |  |  |  |  | R @ 20°c: |  | 4.95 | Ω/kM | FW | 3 | 3.7 | 0.47391 | 4.72 | 0.3144 | 2.469 | 1.08 | 0.47 | 582.1935 |  | 0.08 | -133.5131 | 0.14 | [6 empty] | " | D | 0.38 | 0.5 |  |  | 1.66 |  | 0.92 |  |  | " | D | 0.38 | 0.5 |  |  | 0.37 |  | 0.51
Nominal Voltage (V): |  |  | 230 | V | Phase-Earth Loop Impedance: |  | 12.36 | Ω/kM | FW | 4 | 4.2 | 2.8435 | 4.25 | 0.3213 | 2.7903 | 1.22 | 0.56 | 480.4543 |  | 0.09 | -101.7392 | 0.14 |  | Insulation Working Temp (tp): | 70 | 70 | 70 | °c
Homerun Cable Length: |  |  | 22 | m | Ipsc: |  | 800 | A | FW | 5 | 6.2 | 0.47391 | 1.41 | 0.1574 | 2.9477 | 1.29 | 0.69 | 381.9293 |  | 0.13 | -98.525 | 0.07 |  | Insulation Final Limit Temp: | 160 | 160 | 160 | °c
Max VD: |  |  | 1.85 | % | I²t or A²s: |  | 2100 |  | FW | 6 | 3.7 | 0.47391 | 0.94 | 0.0626 | 3.0103 | 1.31 | 0.77 | 340.2857 |  | 0.08 | -41.6436 | 0.02
Disconnection Time: |  |  | 0.4 | s | K²S²: |  | 327184 |  | FW | 7 | 3.7 |  | 0.47 | 0.0313 | 3.0416 | 1.33 | 0.85 | 306.8305 |  | 0.08 | -33.4552 | 0.02 |  | Grouping Factor: | 0 | 1 | 1
[5 empty] | K²S²>I²t or A²s: |  | ü |  | FL | 8 | 1 | 0.47391 | 0.47 | 0.015 | 3.0566 | 1.33 | 0.87 | 298.8886 |  | 0.02 | -7.942 | 0 |  |  | 0.7 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Cg: | 0.7 | 1 | 1
CIRCUIT PROTECTIVE DEVICE (CPD): | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Rating (In): |  |  | 10 | A | FLAT WIRING | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | It ≥ | 14.2857 | 10 | 10 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Type (MCB Only): |  |  | C |  | Nº of Circuits/Cables: |  | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [8 empty] | 2.4 | 2.2 | 0 | 0 | 5.33 | 0 | 2.95 | 0 | 0 |  |  | 2.4 | 2.2 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
Manufacturer: |  |  | Schneider |  | CSA: |  | 2.5 | mm² |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | CPD: | Schneider | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tabulated Zs: |  |  | 2.4 | Ω | Insulation: |  | LSFZH | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 5 Sec | 2.95 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Operating Temperature (tp): |  | 70 | °C |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0.4 Sec | 2.4 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Rating (It): |  | 30 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Zs: | 2.4 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Volt Drop (R): |  | 18 | mV/A/m |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | CPD | 2.4 | 2.2 | 0 | 0 | 5.33 | 0 | 2.95 | 0 | 0 |  | CPD | 2.4 | 2.2 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
[5 empty] | R @ 20°c: |  | 7.98 | Ω/kM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail MDB Cg: | ü
[5 empty] | Phase-Earth Loop Impedance: |  | 19.92 | Ω/kM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Cg: |  | ü |  |  |  | Schneider | [10 empty] | Schneider
[5 empty] | Ipsc Max: |  | 800 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Cg: |  |  | ü
| This calculation is un-checked |  |  |  | Ipsc Min: |  | 298.8886 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail VD: | ü | ü | ü
[5 empty] | I²t or A²s Max: |  | 2100 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Zs: | ü | û | û |  |  |  | 20A Type C |  | 10A Type C
[5 empty] | I²t or A²s Min: |  | 300 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SWITCH DROP/UN-ARMOURED CABLE: | Pass/Fail Home-Run Ipsc: | ü | [5 empty] | Ipsc | A²s | Ipsc | A²s
[5 empty] | K²S²: |  | 127806.25 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SERVICE DROP CABLE: | Pass/Fail Extender Max Ipsc: | ü
[5 empty] | K²S²>I²t or A²s Max: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Min Ipsc: | ü |  |  |  |  | 1 | 100 | 70 | 100 | 70
[5 empty] | K²S²>I²t or A²s Min: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Ipsc: | ü |  |  |  |  | 2 | 200 | 300 | 200 | 300
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | 3 | 300 | 500 | 300 | 500
[20 empty] | 0.87 | 298.8886 | 1.33 |  | Supply Voltage Drop: | 2.15% |  |  |  |  | 4 | 400 | 980 | 400 | 980
[5 empty] | FLYING LEAD |  |  |  | KEY: | [5 empty] | CIRCUIT CHECK: |  |  | OK | [5 empty] | Supply Voltage Drop: | 4.945 |  |  |  |  | 5 | 500 | 1200 | 500 | 1200
[5 empty] | Nº of Circuits/Cables: |  | 1 |  | FW = Flat Wiring | [5 empty] | Homerun Overload Protection: |  |  | ü | [5 empty] | Supply Voltage: | 229.5055 |  |  |  |  | 6 | 600 | 1500 | 600 | 1500
[5 empty] | CSA: |  | 1.5 | mm² | FL = Flying Lead | [5 empty] | Extender Overload Protection: |  |  | ü | [11 empty] | 7 | 700 | 2000 | 700 | 2000
[5 empty] | Insulation: |  | LSFZH | [7 empty] | SD/RL Overload Protection: |  |  | ü | [11 empty] | 8 | 800 | 2100 | 800 | 2100
[5 empty] | Operating Temperature (tp): |  | 70 | °C | [6 empty] | Voltage Drop less than 1.85%: |  |  | ü | [11 empty] | 9 | 900 | 2500 | 900 | 2500
[5 empty] | Rating (It): |  | 16 | A | [6 empty] | Calculated Zs less than Tab Zs: |  |  | ü | [11 empty] | 10 | 1000 | 2800 | 1000 | 2800
[5 empty] | Volt Drop (R): |  | 32 | mV/A/m | [21 empty] | 11 | 2000 | 6000 | 2000 | 6000
[5 empty] | R @ 20°c: |  | 13.3 | Ω/kM | [21 empty] | 12 | 3000 | 8400 | 3000 | 8400
| RESULTS SUMMARY |  |  |  | Phase-Earth Loop Impedance: |  | 33.2 | Ω/kM | [21 empty] | 13 | 4000 | 10000 | 4000 | 10000
| Load: |  | 7.56 |  | Ipsc: |  | 298.8886 | A | NOTES:
| Length: |  | 46.2 |  | I²t or A²s: |  | 300 |  | 1. Based upon Ambient Temperature of 30°C.
| Zs: |  | 0.87 |  | K²S²: |  | 46010.25 |  | 2. Zs vaule @ source based upon Transfomrer Supply. | [20 empty] | Home-Run: | 800
| Ipsc: |  | 298.8886 |  | K²S²>I²t or A²s: |  | ü |  | 3. Ipsc vaule @ source based upon Transformer Supply (max figure). | [20 empty] | Extender Max: | 800 |  | Thermal Withstand Model
| Voltage Drop: |  | 3.0566 | [5 empty] | 4. Thermal-Withstand current levels taken at MDB, end of 1st Extender & end of circuit leg. | [20 empty] | Extender Min: | 298.8886
| Final Voltage: |  | 221.9984 | [26 empty] | SD: | 298.8886
[31 empty] | Home-Run |  | Extender Max |  | Extender Min
[30 empty] | 13 | 0 |  | 0 |  | 0
[30 empty] | 12 | 0 |  | 0 |  | 0
[30 empty] | 11 | 0 |  | 0 |  | 0
[30 empty] | 10 | 0 |  | 0 |  | 0
[30 empty] | 9 | 0 |  | 0 |  | 0
[30 empty] | 8 | 2100 |  | 2100 |  | 0
[30 empty] | 7 | 0 |  | 0 |  | 0
[30 empty] | 6 | 0 |  | 0 |  | 0
[30 empty] | 5 | 0 |  | 0 |  | 0
[30 empty] | 4 | 0 |  | 0 |  | 0
[30 empty] | 3 | 0 |  | 0 |  | 0
[30 empty] | 2 | 0 |  | 0 |  | 300
[30 empty] | 1 | 0 |  | 0 |  | 0
[30 empty] | Value: | 2100 |  | 2100 |  | 300
Note on J15: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on J16: Enter: 2.50 4.00 6.00
Note on J17: Enter: XL-LSFZH LSFZH
Note on D30: Enter: B C D
Note on J30: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on D31: Enter: BS7671 ABB Hager Schneider
Note on J31: Enter: 1.50 2.50 4.00
Note on J32: Enter: XL-LSFZH LSFZH
Note on J48: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on J49: Enter: 1.50 2.50 4.00
Note on J50: Enter: XL-LSFZH LSFZH

## 14L3
[8 empty] | © The ARK Electrical Design Co. | [10 empty] | © The ARK Electrical Design Co. | [15 empty] | Tabulated Zs Figures for 5 Second Disconnection Time | [10 empty] | Tabulated Zs Figures for 0.4 Second Disconnection Time
[29 empty] | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
CIRCUIT CALCULATION SHEET: | [8 empty] | CIRCUIT CALCULATION SHEET: | [13 empty] | Short-Circuit Withstand | [7 empty] | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D |  |  | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
Project Name: |  | Fife-JV |  |  |  | Prepared By: | N Holmes |  | Project Name: |  | Fife-JV | [5 empty] | Prepared By: | N Holmes |  |  |  |  | Is Ipsc trip time > 0.1s | [5 empty] | 6A | B | 8 | 7.7 |  |  | 8.8 |  | 7.6 |  |  | 6A | B | 8 | 7.7 |  |  | 8 |  | 7.6
Project Nº: |  | MW502 |  |  |  | Date Prepared: | 26.06.10 |  | Project Nº: |  | MW502 | [5 empty] | Date Prepared: | 26.06.10 |  |  |  |  | If YES, then I²S² from ABB required |  | FEEDER | FLAT WIRING | FLYING LEAD |  | " | C | 4 | 3.8 |  |  | 8.8 |  | 4.89 |  |  | " | C | 4 | 3.8 |  |  | 4 |  | 3.88
Area/Zone/Level: |  | Level 00 - DB Zone E1¦0¦BL |  |  |  | Revision: | C1 |  | Area/Zone/Level: |  | Level 00 - DB Zone E1¦0¦BL | [5 empty] | Revision: | C1 |  |  |  |  | K²S²>A²s | It (Tab): | 34 | 30 | 16 |  | " | D | 2 | 2.7 |  |  | 8.8 |  | 4.89 |  |  | " | D | 2 | 2.7 |  |  | 1 |  | 2.74
Drawing Nº: |  | CD-MS-02-L(62)1-XX-006 |  |  |  | Checked By: |  |  | Drawing Nº: |  | CD-MS-02-L(62)1-XX-006 | [5 empty] | Checked By: | 0 |  |  |  |  | Establish the typical range of A²s from ABB for the range of Ipsc | [5 empty] | 10A | B | 4.8 | 4.6 |  |  | 5.33 |  | 4.6 |  |  | 10A | B | 4.8 | 4.6 |  |  | 4.8 |  | 4.6
Service: |  | Lighting |  |  |  |  | UCVD May 2010 V4.3 |  | Service: |  | Lighting | [6 empty] | UCVD May 2010 V4.3 | [5 empty] | Voltage Drop (Tab): | 12 | 18 | 32 |  | " | C | 2.4 | 2.2 |  |  | 5.33 |  | 2.95 |  |  | " | C | 2.4 | 2.2 |  |  | 2.4 |  | 2.3
[29 empty] | " | D | 1.2 | 1.6 |  |  | 5.33 |  | 2.95 |  |  | " | D | 1.2 | 1.6 |  |  | 1.2 |  | 1.64
DB Ref: |  | 2 | [6 empty] | DB Ref: |  | 2 | [12 empty] | R@20²C (Tab): | 4.95 | 7.98 | 13.3 |  | 16A | B | 3 | 2.9 |  |  | 3.33 |  | 2.88 |  |  | 16A | B | 3 | 2.9 |  |  | 3 |  | 2.88
[9 empty] | 0 |  | 0 | [17 empty] | " | C | 1.5 | 1.4 |  |  | 3.33 |  | 1.84 |  |  | " | C | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
Circuit Ref: |  | 2¦14L3 | [6 empty] | Circuit Ref: |  | 2¦14L3 | [12 empty] | Zinst_PHASE: | 6.1776 | 9.959 | 16.5984 |  | " | D | 0.75 | 1 |  |  | 3.33 |  | 1.84 |  |  | " | D | 0.75 | 1 |  |  | 0.75 |  | 1.03
[24 empty] | Zinst_CPC: | 6.1776 | 9.959 | 16.5984 |  | 20A | B | 2.4 | 2.3 |  |  | 2.66 |  | 2.3 |  |  | 20A | B | 2.4 | 2.3 |  |  | 2.4 |  | 2.3
DISTRIBUTION BOARD: |  |  |  |  | FEEDER CABLE: |  |  |  | CIRCUIT INPUT DATA: | [19 empty] | " | C | 1.2 | 1.2 |  |  | 2.66 |  | 1.47 |  |  | " | C | 1.2 | 1.2 |  |  | 1.2 |  | 1.15
Voltage Drop: |  |  | 2.15 | % | Nº of Circuits per MDB: |  | 12 | [16 empty] | CPD_R_Factor: | 1.248 | 1.248 | 1.248 |  | " | D | 0.6 | 0.8 |  |  | 2.66 |  | 1.47 |  |  | " | D | 0.6 | 0.8 |  |  | 0.6 |  | 0.82
Actual Voltage: |  |  | 225.055 | V | CSA: |  | 4 | mm² | CABLE | CABLE | LENGTH | LOAD (A) |  |  | VOLTAGE DROP (V) |  | Zs | Ipsc | [10 empty] | 25A | B | 1.8 | 1.8 |  |  | 2.14 |  | 1.84 |  |  | 25A | B | 1.8 | 1.8 |  |  | 1.92 |  | 1.84
Fault Current @ DB (Ipsc): |  |  | 14430 | A | Insulation: |  | LSFZH |  | TYPE | LEG | Metres | Per Leg | Total | Per Leg | Total | % | (W) | (A) |  | Zs | Ipsc | %VoltDrop |  | Ambient T (IEE GN5 Table B1): | 1.04 | 1.04 | 1.04 |  | " | C | 1 | 0.9 |  |  | 2.14 |  | 1.18 |  |  | " | C | 1 | 0.9 |  |  | 0.96 |  | 0.92
External P/E Loop (Ze): |  |  | 0.07373 | Ω | Operating Temperature (tp): |  | 70 | °C | Feeder | - | 19 | - | 6.13 | 1.3976 | 1.3976 | 0.61 | 0.31 | 918 |  | 0.31 | 918 | 0.61 |  | Temp Factor F (IEE GN5 Table B2): | 1.2 | 1.2 | 1.2 |  | " | D | 0.46 | 0.7 |  |  | 2.14 |  | 1.18 |  |  | " | D | 0.46 | 0.7 |  |  | 0.48 |  | 0.66
[5 empty] | Rating (It): |  | 34 | A | FW | 1 | 0 | 2.3696 | 6.13 | 0 | 1.3976 | 0.61 | 0.31 | 918 |  | 0 | 1.1369e-13 | 0 |  | Total Factor: | 1.248 | 1.248 | 1.248 |  | 32A | B | 1.5 | 1.4 |  |  | 1.66 |  | 1.44 |  |  | 32A | B | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
[5 empty] | Volt Drop (R): |  | 12 | mV/A/m | FW | 2 | 1.7 | 0.47391 | 3.76 | 0.1151 | 1.5127 | 0.66 | 0.35 | 808.7048 |  | 0.04 | -109.2952 | 0.05 | [6 empty] | " | C | 0.75 | 0.7 |  |  | 1.66 |  | 0.92 |  |  | " | C | 0.75 | 0.7 |  |  | 0.75 |  | 0.72
CIRCUIT DESIGN: |  |  |  |  | R @ 20°c: |  | 4.95 | Ω/kM | FW | 3 | 3.7 | 0.47391 | 3.29 | 0.2191 | 1.7318 | 0.76 | 0.43 | 642.2746 |  | 0.08 | -166.4302 | 0.1 | [6 empty] | " | D | 0.38 | 0.5 |  |  | 1.66 |  | 0.92 |  |  | " | D | 0.38 | 0.5 |  |  | 0.37 |  | 0.51
Nominal Voltage (V): |  |  | 230 | V | Phase-Earth Loop Impedance: |  | 12.36 | Ω/kM | FW | 4 | 3.2 | 0.47391 | 2.82 | 0.1624 | 1.8942 | 0.83 | 0.5 | 545.2302 |  | 0.07 | -97.0444 | 0.07 |  | Insulation Working Temp (tp): | 70 | 70 | 70 | °c
Homerun Cable Length: |  |  | 19 | m | Ipsc: |  | 918 | A | FW | 5 | 5.2 | 0.47391 | 2.35 | 0.22 | 2.1142 | 0.92 | 0.61 | 437.7499 |  | 0.11 | -107.4803 | 0.09 |  | Insulation Final Limit Temp: | 160 | 160 | 160 | °c
Max VD: |  |  | 1.85 | % | I²t or A²s: |  | 2500 |  | FW | 6 | 3.7 | 0.47391 | 1.88 | 0.1252 | 2.2394 | 0.98 | 0.69 | 383.9021 |  | 0.08 | -53.8478 | 0.06
Disconnection Time: |  |  | 0.4 | s | K²S²: |  | 327184 |  | FW | 7 | 3.7 | 0.47391 | 1.41 | 0.0939 | 2.3333 | 1.02 | 0.77 | 341.8509 |  | 0.08 | -42.0512 | 0.04 |  | Grouping Factor: | 0 | 1 | 1
[5 empty] | K²S²>I²t or A²s: |  | ü |  | FW | 8 | 3.7 | 0.47391 | 0.94 | 0.0626 | 2.3959 | 1.05 | 0.85 | 308.1025 |  | 0.08 | -33.7484 | 0.03 |  |  | 0.7 | 0 | 0
[9 empty] | FW | 9 | 3.7 |  | 0.47 | 0.0313 | 2.4272 | 1.06 | 0.93 | 280.4188 |  | 0.08 | -27.6837 | 0.01 |  | Cg: | 0.7 | 1 | 1
CIRCUIT PROTECTIVE DEVICE (CPD): | [8 empty] | FL | 10 | 1 | 0.47391 | 0.47 | 0.015 | 2.4422 | 1.07 | 0.95 | 273.7705 |  | 0.02 | -6.6483 | 0.01
Rating (In): |  |  | 10 | A | FLAT WIRING | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | It ≥ | 14.2857 | 10 | 10 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Type (MCB Only): |  |  | C |  | Nº of Circuits/Cables: |  | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [8 empty] | 2.4 | 2.2 | 0 | 0 | 5.33 | 0 | 2.95 | 0 | 0 |  |  | 2.4 | 2.2 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
Manufacturer: |  |  | Schneider |  | CSA: |  | 2.5 | mm² |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | CPD: | Schneider | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tabulated Zs: |  |  | 2.4 | Ω | Insulation: |  | LSFZH | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 5 Sec | 2.95 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Operating Temperature (tp): |  | 70 | °C |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0.4 Sec | 2.4 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Rating (It): |  | 30 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Zs: | 2.4 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Volt Drop (R): |  | 18 | mV/A/m |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | CPD | 2.4 | 2.2 | 0 | 0 | 5.33 | 0 | 2.95 | 0 | 0 |  | CPD | 2.4 | 2.2 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
[5 empty] | R @ 20°c: |  | 7.98 | Ω/kM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail MDB Cg: | ü
[5 empty] | Phase-Earth Loop Impedance: |  | 19.92 | Ω/kM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Cg: |  | ü |  |  |  | Schneider | [10 empty] | Schneider
[5 empty] | Ipsc Max: |  | 918 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Cg: |  |  | ü
| This calculation is un-checked |  |  |  | Ipsc Min: |  | 273.7705 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail VD: | ü | ü | ü
[5 empty] | I²t or A²s Max: |  | 2500 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Zs: | ü | û | û |  |  |  | 20A Type C |  | 10A Type C
[5 empty] | I²t or A²s Min: |  | 300 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SWITCH DROP/UN-ARMOURED CABLE: | Pass/Fail Home-Run Ipsc: | ü | [5 empty] | Ipsc | A²s | Ipsc | A²s
[5 empty] | K²S²: |  | 127806.25 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SERVICE DROP CABLE: | Pass/Fail Extender Max Ipsc: | ü
[5 empty] | K²S²>I²t or A²s Max: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Min Ipsc: | ü |  |  |  |  | 1 | 100 | 70 | 100 | 70
[5 empty] | K²S²>I²t or A²s Min: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Ipsc: | ü |  |  |  |  | 2 | 200 | 300 | 200 | 300
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | 3 | 300 | 500 | 300 | 500
[20 empty] | 0.95 | 273.7705 | 1.07 |  | Supply Voltage Drop: | 2.15% |  |  |  |  | 4 | 400 | 980 | 400 | 980
[5 empty] | FLYING LEAD |  |  |  | KEY: | [5 empty] | CIRCUIT CHECK: |  |  | OK | [5 empty] | Supply Voltage Drop: | 4.945 |  |  |  |  | 5 | 500 | 1200 | 500 | 1200
[5 empty] | Nº of Circuits/Cables: |  | 1 |  | FW = Flat Wiring | [5 empty] | Homerun Overload Protection: |  |  | ü | [5 empty] | Supply Voltage: | 229.5055 |  |  |  |  | 6 | 600 | 1500 | 600 | 1500
[5 empty] | CSA: |  | 1.5 | mm² | FL = Flying Lead | [5 empty] | Extender Overload Protection: |  |  | ü | [11 empty] | 7 | 700 | 2000 | 700 | 2000
[5 empty] | Insulation: |  | LSFZH | [7 empty] | SD/RL Overload Protection: |  |  | ü | [11 empty] | 8 | 800 | 2100 | 800 | 2100
[5 empty] | Operating Temperature (tp): |  | 70 | °C | [6 empty] | Voltage Drop less than 1.85%: |  |  | ü | [11 empty] | 9 | 900 | 2500 | 900 | 2500
[5 empty] | Rating (It): |  | 16 | A | [6 empty] | Calculated Zs less than Tab Zs: |  |  | ü | [11 empty] | 10 | 1000 | 2800 | 1000 | 2800
[5 empty] | Volt Drop (R): |  | 32 | mV/A/m | [21 empty] | 11 | 2000 | 6000 | 2000 | 6000
[5 empty] | R @ 20°c: |  | 13.3 | Ω/kM | [21 empty] | 12 | 3000 | 8400 | 3000 | 8400
| RESULTS SUMMARY |  |  |  | Phase-Earth Loop Impedance: |  | 33.2 | Ω/kM | [21 empty] | 13 | 4000 | 10000 | 4000 | 10000
| Load: |  | 6.13 |  | Ipsc: |  | 273.7705 | A | NOTES:
| Length: |  | 48.6 |  | I²t or A²s: |  | 300 |  | 1. Based upon Ambient Temperature of 30°C.
| Zs: |  | 0.95 |  | K²S²: |  | 46010.25 |  | 2. Zs vaule @ source based upon Transfomrer Supply. | [20 empty] | Home-Run: | 918
| Ipsc: |  | 273.7705 |  | K²S²>I²t or A²s: |  | ü |  | 3. Ipsc vaule @ source based upon Transformer Supply (max figure). | [20 empty] | Extender Max: | 918 |  | Thermal Withstand Model
| Voltage Drop: |  | 2.4422 | [5 empty] | 4. Thermal-Withstand current levels taken at MDB, end of 1st Extender & end of circuit leg. | [20 empty] | Extender Min: | 273.7705
| Final Voltage: |  | 222.6128 | [26 empty] | SD: | 273.7705
[31 empty] | Home-Run |  | Extender Max |  | Extender Min
[30 empty] | 13 | 0 |  | 0 |  | 0
[30 empty] | 12 | 0 |  | 0 |  | 0
[30 empty] | 11 | 0 |  | 0 |  | 0
[30 empty] | 10 | 0 |  | 0 |  | 0
[30 empty] | 9 | 2500 |  | 2500 |  | 0
[30 empty] | 8 | 0 |  | 0 |  | 0
[30 empty] | 7 | 0 |  | 0 |  | 0
[30 empty] | 6 | 0 |  | 0 |  | 0
[30 empty] | 5 | 0 |  | 0 |  | 0
[30 empty] | 4 | 0 |  | 0 |  | 0
[30 empty] | 3 | 0 |  | 0 |  | 0
[30 empty] | 2 | 0 |  | 0 |  | 300
[30 empty] | 1 | 0 |  | 0 |  | 0
[30 empty] | Value: | 2500 |  | 2500 |  | 300
Note on J15: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on J16: Enter: 2.50 4.00 6.00
Note on J17: Enter: XL-LSFZH LSFZH
Note on D30: Enter: B C D
Note on J30: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on D31: Enter: BS7671 ABB Hager Schneider
Note on J31: Enter: 1.50 2.50 4.00
Note on J32: Enter: XL-LSFZH LSFZH
Note on J48: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on J49: Enter: 1.50 2.50 4.00
Note on J50: Enter: XL-LSFZH LSFZH

## 7L3b
Modular Systems + | [7 empty] | © The ARK Electrical Design Co. | Modular Systems + | [9 empty] | © The ARK Electrical Design Co. | [15 empty] | Tabulated Zs Figures for 5 Second Disconnection Time | [10 empty] | Tabulated Zs Figures for 0.4 Second Disconnection Time
[29 empty] | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D | In | Type | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
CIRCUIT CALCULATION SHEET: | [8 empty] | CIRCUIT CALCULATION SHEET: | [13 empty] | Short-Circuit Withstand | [7 empty] | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D |  |  | BS 7671 | ABB | Crabtree | Dorman | Hager | MEM | Schneider | Siemens | Square D
Project Name: |  | Fife-JV |  |  |  | Prepared By: | N Holmes |  | Project Name: |  | Fife-JV | [5 empty] | Prepared By: | N Holmes |  |  |  |  | Is Ipsc trip time > 0.1s | [5 empty] | 6A | B | 8 | 7.7 |  |  | 8.8 |  | 7.6 |  |  | 6A | B | 8 | 7.7 |  |  | 8 |  | 7.6
Project Nº: |  | MW502 |  |  |  | Date Prepared: | 26.06.10 |  | Project Nº: |  | MW502 | [5 empty] | Date Prepared: | 26.06.10 |  |  |  |  | If YES, then I²S² from ABB required |  | HOMERUN | EXTENDER | SERVICE DROP |  | " | C | 4 | 3.8 |  |  | 8.8 |  | 4.89 |  |  | " | C | 4 | 3.8 |  |  | 4 |  | 3.88
Area/Zone/Level: |  | Level 00 - DB Zone E1¦0¦BL |  |  |  | Revision: | C1 |  | Area/Zone/Level: |  | Level 00 - DB Zone E1¦0¦BL | [5 empty] | Revision: | C1 |  |  |  |  | K²S²>A²s | It (Tab): | 40 | 25 | 16 |  | " | D | 2 | 2.7 |  |  | 8.8 |  | 4.89 |  |  | " | D | 2 | 2.7 |  |  | 1 |  | 2.74
Drawing Nº: |  | CD-MS-02-L(62)1-XX-006 |  |  |  | Checked By: |  |  | Drawing Nº: |  | CD-MS-02-L(62)1-XX-006 | [5 empty] | Checked By: | 0 |  |  |  |  | Establish the typical range of A²s from ABB for the range of Ipsc | [5 empty] | 10A | B | 4.8 | 4.6 |  |  | 5.33 |  | 4.6 |  |  | 10A | B | 4.8 | 4.6 |  |  | 4.8 |  | 4.6
Service: |  | Lighting |  |  |  |  | UCVD May 2010 V4.3 |  | Service: |  | Lighting | [6 empty] | UCVD May 2010 V4.3 | [5 empty] | Voltage Drop (Tab): | 12 | 19 | 32 |  | " | C | 2.4 | 2.2 |  |  | 5.33 |  | 2.95 |  |  | " | C | 2.4 | 2.2 |  |  | 2.4 |  | 2.3
[29 empty] | " | D | 1.2 | 1.6 |  |  | 5.33 |  | 2.95 |  |  | " | D | 1.2 | 1.6 |  |  | 1.2 |  | 1.64
DB Ref: |  | 2 | [6 empty] | DB Ref: |  | 2 | [12 empty] | R@20²C (Tab): | 4.61 | 7.98 | 13.3 |  | 16A | B | 3 | 2.9 |  |  | 3.33 |  | 2.88 |  |  | 16A | B | 3 | 2.9 |  |  | 3 |  | 2.88
MDB Nº: |  | 2¦ | 06 | [5 empty] | MDB Nº: |  | 2¦ | [17 empty] | " | C | 1.5 | 1.4 |  |  | 3.33 |  | 1.84 |  |  | " | C | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
Circuit Ref: |  | 2¦7L3b | [6 empty] | Circuit Ref: |  | 2¦7L3b | [12 empty] | Zinst_PHASE: | 6.1368 | 9.959 | 16.5984 |  | " | D | 0.75 | 1 |  |  | 3.33 |  | 1.84 |  |  | " | D | 0.75 | 1 |  |  | 0.75 |  | 1.03
[24 empty] | Zinst_CPC: | 6.1368 | 9.959 | 16.5984 |  | 20A | B | 2.4 | 2.3 |  |  | 2.66 |  | 2.3 |  |  | 20A | B | 2.4 | 2.3 |  |  | 2.4 |  | 2.3
DISTRIBUTION BOARD: |  |  |  |  | HOMERUN CABLE: |  |  |  | CIRCUIT INPUT DATA: | [19 empty] | " | C | 1.2 | 1.2 |  |  | 2.66 |  | 1.47 |  |  | " | C | 1.2 | 1.2 |  |  | 1.2 |  | 1.15
Voltage Drop: |  |  | 2.15 | % | Nº of Circuits per MDB: |  | 6 | [16 empty] | CPD_R_Factor: | 1.3312 | 1.248 | 1.248 |  | " | D | 0.6 | 0.8 |  |  | 2.66 |  | 1.47 |  |  | " | D | 0.6 | 0.8 |  |  | 0.6 |  | 0.82
Actual Voltage: |  |  | 225.055 | V | CSA: |  | 4 | mm² | CABLE | CABLE | LENGTH | LOAD (A) |  |  | VOLTAGE DROP (V) |  | Zs | Ipsc | [10 empty] | 25A | B | 1.8 | 1.8 |  |  | 2.14 |  | 1.84 |  |  | 25A | B | 1.8 | 1.8 |  |  | 1.92 |  | 1.84
Fault Current @ DB (Ipsc): |  |  | 14430 | A | Insulation: |  | XL-LSFZH |  | TYPE | LEG | Metres | Per Leg | Total | Per Leg | Total | % | (W) | (A) |  | Zs | Ipsc | %VoltDrop |  | Ambient T (IEE GN5 Table B1): | 1.04 | 1.04 | 1.04 |  | " | C | 1 | 0.9 |  |  | 2.14 |  | 1.18 |  |  | " | C | 1 | 0.9 |  |  | 0.96 |  | 0.92
External P/E Loop (Ze): |  |  | 0.07373 | Ω | Operating Temperature (tp): |  | 90 | ° | Home Run | - | 59 | - | 3.13 | 2.216 | 2.216 | 0.97 | 0.8 | 311 |  | 0.8 | 311 | 0.97 |  | Temp Factor F (IEE GN5 Table B2): | 1.28 | 1.2 | 1.2 |  | " | D | 0.46 | 0.7 |  |  | 2.14 |  | 1.18 |  |  | " | D | 0.46 | 0.7 |  |  | 0.48 |  | 0.66
[5 empty] | Rating (It): |  | 40 | A | U | 1 | 10 |  | 3.13 | 1.0016 | 3.2176 | 1.4 | 1 | 245.0117 |  | 0.2 | -65.9883 | 0.43 |  | Total Factor: | 1.3312 | 1.248 | 1.248 |  | 32A | B | 1.5 | 1.4 |  |  | 1.66 |  | 1.44 |  |  | 32A | B | 1.5 | 1.4 |  |  | 1.5 |  | 1.44
[5 empty] | Volt Drop (R): |  | 12 | mV/A/m | U | 2 | 10 |  | 3.13 | 1.0016 | 4.2192 | 1.84 | 1.2 | 202.1247 |  | 0.2 | -42.887 | 0.44 | [6 empty] | " | C | 0.75 | 0.7 |  |  | 1.66 |  | 0.92 |  |  | " | C | 0.75 | 0.7 |  |  | 0.75 |  | 0.72
CIRCUIT DESIGN: |  |  |  |  | R @ 20°c: |  | 4.61 | Ω/kM | U | 3 | 9 | 1.0783 | 3.13 | 0.9014 | 5.1206 | 2.23 | 1.38 | 174.6162 |  | 0.18 | -27.5085 | 0.39 | [6 empty] | " | D | 0.38 | 0.5 |  |  | 1.66 |  | 0.92 |  |  | " | D | 0.38 | 0.5 |  |  | 0.37 |  | 0.51
Nominal Voltage (V): |  |  | 230 | V | Phase-Earth Loop Impedance: |  | 12.28 | Ω/kM | U | 4 | 3 |  | 2.05 | 0.1968 | 5.3174 | 2.32 | 1.44 | 167.0385 |  | 0.06 | -7.5778 | 0.09 |  | Insulation Working Temp (tp): | 90 | 70 | 70 | °c
Homerun Cable Length: |  |  | 59 | m | Ipsc: |  | 311 | A | U | 5 | 3 | 0.90435 | 2.05 | 0.1968 | 5.5142 | 2.4 | 1.5 | 160.091 |  | 0.06 | -6.9474 | 0.08 |  | Insulation Final Limit Temp: | 250 | 160 | 160 | °c
Max VD: |  |  | 1.85 | % | I²t or A²s: |  | 500 |  | U | 6 | 2 |  | 1.15 | 0.0736 | 5.5878 | 2.43 | 1.54 | 155.7718 |  | 0.04 | -4.3192 | 0.03
Disconnection Time: |  |  | 0.4 | s | K²S²: |  | 327184 |  | U | 7 | 3 | 0.23478 | 1.15 | 0.1104 | 5.6982 | 2.48 | 1.6 | 149.713 |  | 0.06 | -6.0588 | 0.05 |  | Grouping Factor: | 0.57 | 0 | 1
[5 empty] | K²S²>I²t or A²s: |  | ü |  | U | 8 | 3 | 0.23478 | 0.92 | 0.0883 | 5.7865 | 2.52 | 1.66 | 144.1078 |  | 0.06 | -5.6052 | 0.04 |  |  |  | 0.71 | 0.71
[9 empty] | U | 9 | 3 | 0.23478 | 0.69 | 0.0662 | 5.8527 | 2.55 | 1.72 | 138.9072 |  | 0.06 | -5.2006 | 0.03 |  | Cg: | 0.57 | 0.71 | 1.71
CIRCUIT PROTECTIVE DEVICE (CPD): | [8 empty] | U | 10 | 3 | 0.23478 | 0.46 | 0.0442 | 5.8969 | 2.57 | 1.78 | 134.0689 |  | 0.06 | -4.8383 | 0.02
Rating (In): |  |  | 10 | A | ARMOURED EXTENDER CABLE: |  |  |  | U | 11 | 3 |  | 0.23 | 0.0221 | 5.919 | 2.58 | 1.84 | 129.5563 |  | 0.06 | -4.5126 | 0.01 |  | It ≥ | 17.5439 | 14.0845 | 5.848 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Type (MCB Only): |  |  | C |  | Nº of Circuits/Cables: |  | 10 |  | F | 12 | 1 | 0.23478 | 0.23 | 0.0074 | 5.9264 | 2.58 | 1.86 | 128.1189 |  | 0.02 | -1.4374 | 0 | [8 empty] | 2.4 | 2.2 | 0 | 0 | 5.33 | 0 | 2.95 | 0 | 0 |  |  | 2.4 | 2.2 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
Manufacturer: |  |  | ABB |  | CSA: |  | 2.5 | mm² |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | CPD: | ABB | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tabulated Zs: |  |  | 2.2 | Ω | Insulation: |  | LSFZH | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 5 Sec | 2.2 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Operating Temperature (tp): |  | 70 | ° |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0.4 Sec | 2.2 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Rating (It): |  | 25 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Zs: | 2.2 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Volt Drop (R): |  | 19 | mV/A/m |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | CPD | 2.4 | 2.2 | 0 | 0 | 5.33 | 0 | 2.95 | 0 | 0 |  | CPD | 2.4 | 2.2 | 0 | 0 | 2.4 | 0 | 2.3 | 0 | 0
[5 empty] | R @ 20°c: |  | 7.98 | Ω/kM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail MDB Cg: | ü
[5 empty] | Phase-Earth Loop Impedance: |  | 19.92 | Ω/kM |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Cg: |  | ü |  |  |  | ABB | [10 empty] | ABB
[5 empty] | Ipsc Max: |  | 245.0117 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Cg: |  |  | ü
| This calculation is un-checked |  |  |  | Ipsc Min: |  | 128.1189 | A |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail VD: | û | ü | ü
[5 empty] | I²t or A²s Max: |  | 300 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Zs: | ü | û | û |  |  |  | 20A Type C |  | 10A Type C
[5 empty] | I²t or A²s Min: |  | 70 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SWITCH DROP/UN-ARMOURED CABLE: | Pass/Fail Home-Run Ipsc: | ü | [5 empty] | Ipsc | A²s | Ipsc | A²s
[5 empty] | K²S²: |  | 127806.25 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | SERVICE DROP CABLE: | Pass/Fail Extender Max Ipsc: | ü
[5 empty] | K²S²>I²t or A²s Max: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail Extender Min Ipsc: | ü |  |  |  |  | 1 | 100 | 70 | 100 | 70
[5 empty] | K²S²>I²t or A²s Min: |  | ü | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Pass/Fail SD Ipsc: | ü |  |  |  |  | 2 | 200 | 300 | 200 | 300
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | 3 | 300 | 500 | 300 | 500
[20 empty] | 1.86 | 128.1189 | 2.58 |  | Supply Voltage Drop: | 2.15% |  |  |  |  | 4 | 400 | 980 | 400 | 980
[5 empty] | SWITCH DROP/UN-ARMOURED CABLE: |  |  |  | KEY: | [5 empty] | CIRCUIT CHECK: |  |  | OK | [5 empty] | Supply Voltage Drop: | 4.945 |  |  |  |  | 5 | 500 | 1200 | 500 | 1200
[5 empty] | Nº of Circuits/Cables: |  | 1 |  | A = Armoured Extender Cable | [5 empty] | Homerun Overload Protection: |  |  | ü | [5 empty] | Supply Voltage: | 229.5055 |  |  |  |  | 6 | 600 | 1500 | 600 | 1500
[5 empty] | CSA: |  | 1.5 | mm² | D = Service or Switch Drop | [5 empty] | Extender Overload Protection: |  |  | ü | [11 empty] | 7 | 700 | 2000 | 700 | 2000
[5 empty] | Insulation: |  | LSFZH |  | F = Flying Lead | [5 empty] | SD/RL Overload Protection: |  |  | ü | [11 empty] | 8 | 800 | 2100 | 800 | 2100
[5 empty] | Operating Temperature (tp): |  | 70 | ° | S = Splitter/Tee | [5 empty] | Voltage Drop less than 1.85%: |  |  | û | [11 empty] | 9 | 900 | 2500 | 900 | 2500
[5 empty] | Rating (It): |  | 16 | A | U = Armoured Extender Cable | [5 empty] | Calculated Zs less than Tab Zs: |  |  | ü | [11 empty] | 10 | 1000 | 2800 | 1000 | 2800
[5 empty] | Volt Drop (R): |  | 32 | mV/A/m | [21 empty] | 11 | 2000 | 6000 | 2000 | 6000
[5 empty] | R @ 20°c: |  | 13.3 | Ω/kM | [21 empty] | 12 | 3000 | 8400 | 3000 | 8400
| RESULTS SUMMARY |  |  |  | Phase-Earth Loop Impedance: |  | 33.2 | Ω/kM | [21 empty] | 13 | 4000 | 10000 | 4000 | 10000
| Load: |  | 3.13 |  | Ipsc: |  | 128.1189 | A | NOTES:
| Length: |  | 112 |  | I²t or A²s: |  | 70 |  | 1. Based upon Ambient Temperature of 30°C.
| Zs: |  | 1.86 |  | K²S²: |  | 46010.25 |  | 2. Zs vaule @ source based upon Transfomrer Supply. | [20 empty] | Home-Run: | 311
| Ipsc: |  | 128.1189 |  | K²S²>I²t or A²s: |  | ü |  | 3. Ipsc vaule @ source based upon Transformer Supply (max figure). | [20 empty] | Extender Max: | 245.0117 |  | Thermal Withstand Model
| Voltage Drop: |  | 5.9264 | [5 empty] | 4. Thermal-Withstand current levels taken at MDB, end of 1st Extender & end of circuit leg. | [20 empty] | Extender Min: | 128.1189
| Final Voltage: |  | 219.1286 | [26 empty] | SD: | 128.1189
[31 empty] | Home-Run |  | Extender Max |  | Extender Min
[30 empty] | 13 | 0 |  | 0 |  | 0
[30 empty] | 12 | 0 |  | 0 |  | 0
[30 empty] | 11 | 0 |  | 0 |  | 0
[30 empty] | 10 | 0 |  | 0 |  | 0
[30 empty] | 9 | 0 |  | 0 |  | 0
[30 empty] | 8 | 0 |  | 0 |  | 0
[30 empty] | 7 | 0 |  | 0 |  | 0
[30 empty] | 6 | 0 |  | 0 |  | 0
[30 empty] | 5 | 0 |  | 0 |  | 0
[30 empty] | 4 | 0 |  | 0 |  | 0
[30 empty] | 3 | 500 |  | 0 |  | 0
[30 empty] | 2 | 0 |  | 300 |  | 0
[30 empty] | 1 | 0 |  | 0 |  | 70
[30 empty] | Value: | 500 |  | 300 |  | 70
Note on J15: Enter nº of circuits at MDB (max = 9). This value MUST include all spare capacity.
Note on J16: Enter: 2.50 4.00 6.00
Note on J17: Enter: XL-LSFZH LSFZH
Note on D30: Enter: B C D
Note on J30: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on D31: Enter: BS7671 ABB Hager Schneider
Note on J31: Enter: 1.50 2.50 4.00
Note on J32: Enter: XL-LSFZH LSFZH
Note on J48: Enter number of circuits on basket/tray [For circuits greater than 12, use 12]
Note on J49: Enter: 1.50 2.50 4.00
Note on J50: Enter: XL-LSFZH LSFZH